Expected Results and Statistical Analysis Plan

Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning

What results will be produced, how they will be analysed and shown, and the formulas used

MPhil Thesis, University of Mines and Technology (UMaT), Tarkwa

Supervisor: Prof. John Annan

Prepared: 10 October 2026 (Version 2: symbols defined under every equation; figure catalogue added)

Status: DRAFT FOR APPROVAL - this document contains no results

Companion to: Project_Roadmap.docx (Version 2)

# 1. Purpose of this document

This document fixes, before any analysis is run, what results the project will produce, which statistical tests will be applied, which formulas will be used, which graphs will be drawn and how each result will be judged. Writing this down first is a recognised safeguard: it prevents choosing tests or settings after the results are seen, and it lets the supervisor approve the method before the work begins. Approval of this document is Step 4 of the roadmap.

No result is reported here. Section 12 describes every result table and every graph: the tables are empty templates, and each graph is specified by its type, axes, colours, data source and the environment that draws it. The only measured values quoted (Section 9.4) come from the Simulink verification already run on 3 October 2026 and saved in the project log.

Where a value depends on a standard that is not yet in hand (ratio limits, Duval zone boundaries, typical gas values), it is marked TO VERIFY. It will be transcribed with clause and page in Step 12 of the roadmap, never typed from memory.

# 2. Research questions, hypotheses and the results that answer them

The four research questions come from the approved methodology plan (Project_Methodology_Plan.docx, Section 5.4). Each is turned into a testable statement and linked to the result that will answer it.

| Research question | What is tested | Result that answers it | Method (section) |
| --- | --- | --- | --- |
| RQ1. How does ML accuracy compare with the conventional methods on the same samples with independently confirmed faults? | H0: the ML model and a conventional method have the same error rate on the same samples. | Tables 4.5, 4.6; Figures 4.9, 4.10 | Cochran's Q; McNemar with Holm correction (7.2-7.4) |
| RQ2. Where do the two approaches disagree, and is the disagreement concentrated near the conventional decision boundaries? | H0: distance to the nearest boundary has no effect on the odds of disagreement (β₁ = 0). | Tables 4.7, 4.8; Figures 4.11-4.13 | Cohen's kappa; logistic regression (7.5-7.6) |
| RQ3. How much accuracy is lost with fewer gases, and what is the minimum useful gas panel? | Rule fixed in advance: the smallest subset whose loss in macro-F1 has an upper 95 % bound not above the tolerance δ. | Table 4.9; Figures 4.16, 4.17 | Bootstrap of the loss (8) |
| RQ4. Can one interface return exactly the offline results, quickly enough for interactive use? | Requirement: fidelity 100 %; response time reported as median and 95th percentile. | Table 4.11; Figures 4.20-4.22 | Fidelity and latency (10) |

Which classifier is best is a supporting question, answered by the Friedman and Nemenyi tests on the cross-validation results (Section 7.1; Figures 4.6 and 4.7).

## 2.1 The hypothesis and the result that would support it

The approved hypothesis is: a machine-learning classifier validated without data leakage will diagnose more samples correctly than any single conventional method on the same data, mainly because it gives an answer where conventional methods give none, and the disagreement between the two will be concentrated near the conventional-method decision boundaries.

The hypothesis will be called supported only if all three of the following hold. Otherwise it is reported as partly supported or not supported, exactly as found:

1.  The ML model has a higher strict accuracy than each conventional method, with a Holm-adjusted McNemar p-value below 0.05.

2.  The advantage comes mainly from the cases where the conventional method gives no diagnosis: the gap in conditional accuracy is smaller than the gap in strict accuracy.

3.  The logistic-regression coefficient for boundary distance is negative, with a 95 % confidence interval that excludes zero (samples closer to a boundary are more often disputed).

# 3. Data used for each result

| Role | Dataset | Records before cleaning (verified) | How labels were set | Used for |
| --- | --- | --- | --- | --- |
| Development | Dissanayake, DGA_train.xlsx | 584 | Codes 0-6; origin not documented (decision D7) | Training, tuning and cross-validation (Table 4.4) |
| Internal test | Dissanayake, DGA_test_unseen.xlsx | 70 (10 per class) | Codes 0-6 | First held-out test of all methods |
| Independent benchmark | IEC TC 10, Duval & dePablo (2001), Annex 1 | 117 | Visual inspection of the failed equipment (method-independent) | Main ML-versus-conventional comparison (RQ1, RQ2) |
| External test | Li (2019) | 201 | Text labels; origin unclear | Sensitivity analysis only |

The final counts after cleaning, scope filtering and de-duplication are not known yet. They will be reported in Table 4.1 and Figure 3.2, together with every exclusion and its reason.

## 3.1 Scoring on the IEC TC 10 benchmark

The IEC TC 10 tables have no Normal class, and they combine the thermal faults T1 and T2 in one table. To compare fairly, the benchmark is scored on five merged classes: PD, D1, D2, T1/T2 and T3. A prediction of T1 or of T2 counts as T1/T2. A prediction of Normal on a benchmark record counts as wrong.

## 3.2 Known threats to validity (to be reported in the thesis)

•  Home advantage for the conventional methods. Duval and dePablo (2001, p. 32) state that the IEC 60599 ratio limits were made more precise using the data of Annex 1 - the same IEC TC 10 cases used here as the benchmark. Conventional accuracy on this benchmark may therefore be optimistic. This will be stated next to every benchmark result.

•  Label origin of the Dissanayake files is not documented (decision D7). If the labels turn out to be method-derived, the internal-test result is reported as supporting evidence only.

•  Small classes. Some benchmark classes are small (for example 9 PD cases before filtering), so per-class results will carry wide confidence intervals and will not be over-interpreted.

•  No Normal output. Conventional methods do not give a Normal class by themselves; a normality gate (Section 4.4) is added so they can be scored on records labelled Normal.

## 3.3 Missing values

A dash or a blank in a source table is recorded as missing, never as zero. Proposed rule, for approval: the primary analysis uses records with all five gases present; a sensitivity analysis treats a missing value as not detected (0 ppm) and is reported beside it. A conventional method returns ND (no diagnosis) whenever a gas it needs is missing.

# 4. Formulas for the conventional DGA methods

These formulas only define the quantities. The decision limits that turn them into a diagnosis are read from the tables in 02_Standards (TO VERIFY until transcribed from IEC 60599, IEEE C57.104-2019 and the Duval Triangle source). The same definitions are already coded in gas_ratios.m and duval_xy.m. All gas concentrations are in parts per million (ppm).

How the symbols are explained: every equation is followed by a 'where' list giving the meaning and unit of each symbol in it. A few standard symbols mean different things in different parts of the work - for example K is the number of classes in Sections 5 and 6 but the load factor in Section 9, and H is the Kruskal-Wallis statistic in Section 6 but the hot-spot factor in Section 9. The list directly under an equation always gives the meaning that applies to that equation.

## 4.1 Gas ratios

The three basic ratios used by both the Rogers and the IEC 60599 methods (ratio names follow the IEEE C57.104 convention, TO VERIFY):

R1=CH4H2  R2=C2H2C2H4  R5=C2H4C2H6#1

where:

R1  –  ratio of the methane concentration to the hydrogen concentration (dimensionless)

R2  –  ratio of the acetylene concentration to the ethylene concentration (dimensionless)

R5  –  ratio of the ethylene concentration to the ethane concentration (dimensionless)

H2  –  concentration of hydrogen dissolved in the oil [ppm]

CH4  –  concentration of methane [ppm]

C2H2  –  concentration of acetylene [ppm]

C2H4  –  concentration of ethylene [ppm]

C2H6  –  concentration of ethane [ppm]

Two further ratios (Doernenburg) are used only as machine-learning features:

R3=C2H2CH4  R4=C2H6C2H2#2

where:

R3  –  ratio of the acetylene concentration to the methane concentration (dimensionless)

R4  –  ratio of the ethane concentration to the acetylene concentration (dimensionless)

The gas concentrations are as defined under Equation (1).

In simple words: each ratio compares two gases. Different faults produce gases in different proportions, so the ratios act as a fingerprint of the fault. A ratio whose denominator is zero is undefined and is reported as missing.

## 4.2 Duval Triangle 1

SD=CH4+C2H4+C2H2#3

where:

SD  –  sum of the methane, ethylene and acetylene concentrations - the only three gases used by Duval Triangle 1 [ppm]

%CH4=100⋅CH4SD  %C2H4=100⋅C2H4SD  %C2H2=100⋅C2H2SD#4

where:

%CH4,  %C2H4,  %C2H2  –  share of each of the three gases in SD [%]; the three shares always add up to 100 %

To plot a sample, the percentages are turned into coordinates in an equilateral triangle of side 1, exactly as coded in duval_xy.m:

x=%C2H4+0.5⋅%CH4100  y=32⋅%CH4100#5

where:

x  –  horizontal coordinate of the sample point: 0 at the 100 % C2H2 corner (bottom left) and 1 at the 100 % C2H4 corner (bottom right) (dimensionless)

y  –  vertical coordinate of the sample point: 0 on the base and 32 at the 100 % CH4 corner (top) (dimensionless)

In simple words: the three percentages always add up to 100, so each sample is one point in the triangle. The triangle is divided into fault zones; the zone that contains the point is the diagnosis.

## 4.3 Decision rule, no-diagnosis cases and coverage

A method gives a fault class when the sample falls inside one code region or zone; otherwise it gives ND (no diagnosis). ND is a result, not an error, and is never removed.

U=nNDN  Coverage=1-U#6

where:

U  –  unresolved (no-diagnosis) rate of a method (fraction, 0 to 1)

nND  –  number of test records for which the method gives no diagnosis (count)

N  –  number of test records (count)

Coverage  –  share of the test records that receive a diagnosis (fraction, 0 to 1)

Astrict=ncorrectN  Acond=ncorrectN-nND#7

where:

Astrict  –  strict accuracy: correct diagnoses divided by all test records, with every ND counted as wrong (fraction)

Acond  –  conditional accuracy: correct diagnoses divided by the records that received a diagnosis (fraction)

ncorrect  –  number of test records diagnosed correctly (count)

N and nND are as defined under Equation (6).

In simple words: strict accuracy counts every ND as a wrong answer (the engineer got no help); conditional accuracy looks only at the cases where the method answered. Both are reported together with coverage, because a method can be accurate when it answers but answer rarely.

Duval Triangle 1 also contains a DT zone (a mixture of electrical and thermal faults), which has no matching class in the datasets. Proposed rule, for approval: a DT result counts as a diagnosis, but as a wrong one, and the number of DT results is reported separately.

## 4.4 Normality gate

y=Normal  if  xg≤xgtyp for every gas g#8

where:

y  –  class given by the conventional method for the sample

g  –  index of a gas: H2, CH4, C2H6, C2H4 or C2H2

xg  –  measured concentration of gas g in the sample [ppm]

xgtyp  –  typical (90 % normal) concentration of gas g for the equipment type, from IEC 60599 [ppm] (TO VERIFY)

Duval and dePablo (2001, p. 32) explain that when all gases are below their typical values, gas ratios should not be calculated, because any fault indication would have no significance. The gate applies this rule so that conventional methods can be scored on Normal records.

## 4.5 Distance to the nearest decision boundary

This value is needed to test the boundary hypothesis (RQ2). For the ratio methods, distance is measured on a log scale, because ratio limits are spread over several decades:

dR=minj,llog10Rj-log10Lj,l#9

where:

dR  –  distance from the sample to the nearest limit in the ratio code table, measured in decades of the ratio (log10 units)

j  –  index of the ratio (R1, R2 or R5)

l  –  index of a limit of ratio j in the code table

Rj  –  value of ratio j for the sample (dimensionless)

Lj,l  –  the l-th limit of ratio j, read from 02_Standards (dimensionless)

log10  –  logarithm to base 10

For the Duval Triangle, distance is the shortest distance from the sample point to any zone edge, in percentage units:

dD=mine∈EdistP,e#10

where:

dD  –  distance from the sample point to the nearest zone edge of the Duval Triangle [percentage points]

P  –  the sample point, located by its three percentages (Equation 4)

e  –  one zone edge: a straight line segment between two neighbouring zone vertices

E  –  the set of all zone edges, read from duval_triangle_zones.csv

distP,e  –  shortest distance from P to the segment e [percentage points]

In simple words: a small distance means the sample sits close to a line on the chart, where a small measurement error could change the diagnosis.

# 5. Machine-learning preprocessing and model design

## 5.1 Feature sets

Gas concentrations are strongly skewed (a few very large values), so they are log-transformed. Every transform is fitted on the training folds only.

xg=log10xg+1#11

where:

xg  –  log-transformed concentration of gas g (log10 of ppm)

xg  –  measured concentration of gas g [ppm]

1  –  offset added so that a zero concentration gives 0 instead of minus infinity

pg=100⋅xgh=15xh#12

where:

pg  –  share of gas g in the total of the five gases [%]

h  –  summation index running over the five gases

xh  –  measured concentration of gas h [ppm]

zg=xg-μgσg#13

where:

zg  –  standardised (scaled) value of feature g (dimensionless)

μg  –  mean of xg over the records of the training fold

σg  –  standard deviation of xg over the records of the training fold

Four feature sets are compared:

| Set | Features | Purpose |
| --- | --- | --- |
| F1 | Log-transformed gases (5 features) | The raw measured information |
| F2 | Relative percentage of each gas (5 features) | A fault fingerprint that does not depend on the total gas level |
| F3 | Ratios R1 to R5 (log scale) and Duval percentages | The engineering knowledge built into the conventional methods |
| F4 | F1 + F2 + F3 | Everything together |

## 5.2 Classifiers and settings to be tuned (proposed, for approval)

| Model | Settings tuned | Proposed search values |
| --- | --- | --- |
| Majority-class baseline | None | Reference floor: always predicts the most common class |
| Support Vector Machine (RBF kernel) | C, gamma | C in {0.1, 1, 10, 100}; gamma in {0.001, 0.01, 0.1, 1, scale} |
| Random Forest | Depth, minimum leaf size | 500 trees; depth in {none, 5, 10}; minimum leaf in {1, 2, 5} |
| XGBoost | Learning rate, depth, rounds | Rate in {0.03, 0.1, 0.3}; depth in {2, 4, 6}; rounds in {100, 300} |
| Neural network (MLP) | Hidden layers, L2 penalty | Layers (16), (32), (32, 16); penalty in {0.0001, 0.001, 0.01} |
| Fifth model (decision D6) | k for k-NN, or C for logistic regression | k in {3, 5, 7, 9}; or C in {0.1, 1, 10} |

## 5.3 Class imbalance

wc=NK⋅nc#14

where:

wc  –  weight given to every training record of class c (dimensionless)

N  –  number of training records (count)

K  –  number of classes: 7 when Normal is included, 6 without it (count)

nc  –  number of training records in class c (count)

c  –  class index

With these weights every class carries the same total weight in training. If oversampling (SMOTE; Chawla et al., 2002) is approved, it is applied inside the training folds only, never to validation or test data.

## 5.4 Validation design (proposed, for approval)

•  Outer loop: stratified 5-fold cross-validation repeated 10 times on the development set, giving 50 performance estimates per model.

•  Inner loop: stratified 5-fold cross-validation inside each outer training part, used only to choose the settings (nested cross-validation; Varma and Simon, 2006).

•  Score used for tuning: macro-F1.

•  One fixed random seed, saved in folds.csv and in every experiment folder.

•  Model-selection rule: the highest mean outer-fold macro-F1; if the best model and the next are not significantly different (Section 7.1), the simpler model is chosen.

•  The internal test set, the IEC TC 10 benchmark and the external Li set are each used once, after the final model has been chosen.

# 6. Performance measures

All measures below are computed from the confusion matrix, the table that counts, for every true class, how many records were given each predicted class.

Precc=TPcTPc+FPc  Recc=TPcTPc+FNc#15

where:

Precc  –  precision of class c: of the records predicted as c, the share that truly are c (fraction)

Recc  –  recall of class c: of the records that truly are c, the share predicted as c (fraction)

TPc  –  true positives: records of class c predicted as c (count)

FPc  –  false positives: records of another class predicted as c (count)

FNc  –  false negatives: records of class c predicted as another class or given ND (count)

F1c=2 PreccReccPrecc+Recc#16

where:

F1c  –  F1-score of class c: the harmonic mean of its precision and recall (fraction, 0 to 1)

Macro-F1=1Kc=1KF1c#17

where:

Macro-F1  –  unweighted mean of the per-class F1-scores (fraction, 0 to 1)

K  –  number of classes (count)

Accuracy=1Nc=1Kncc  Balanced accuracy=1Kc=1KRecc#18

where:

Accuracy  –  share of all records classified correctly (fraction)

ncc  –  records of class c predicted as c, i.e. the diagonal cells of the confusion matrix (count)

N  –  number of records (count)

Balanced accuracy  –  mean of the per-class recalls (fraction)

κ=po-pe1-pe  pe=1N2c=1Knc+n+c#19

where:

κ  –  Cohen's kappa: agreement beyond chance (from −1 to 1; 0 means chance-level agreement)

po  –  observed proportion of records on which the two raters agree (fraction)

pe  –  proportion of agreement expected by chance alone (fraction)

nc+  –  number of records placed in class c by the first rater - the truth, or method A (count)

n+c  –  number of records placed in class c by the second rater - method B (count)

N  –  number of records (count)

MCC=ncorrect⋅N-kpktkN2-kpk2N2-ktk2#20

where:

MCC  –  multi-class Matthews correlation coefficient (Gorodkin, 2004), from −1 to 1; 1 = perfect, 0 = no better than chance

ncorrect  –  number of correct predictions (count)

N  –  number of records (count)

pk  –  number of times class k was predicted (count)

tk  –  number of times class k truly occurs (count)

k  –  class index

## 6.1 Primary and secondary measures

•  Primary measure: macro-F1. It gives every fault class equal importance, so a model cannot look good by being right only on the common classes.

•  Secondary measures: balanced accuracy; strict and conditional accuracy; coverage; Cohen's kappa; MCC; per-class precision, recall and F1; the confusion matrix.

## 6.2 Confidence intervals

For a proportion such as accuracy or coverage, the Wilson score interval is used (Wilson, 1927), because it behaves well for small samples:

CI95=p+z22n±zp1-pn+z24n21+z2n#21

where:

CI95  –  lower and upper limits of the 95 % Wilson interval (one from each sign of ±)

p  –  observed proportion, for example accuracy or coverage (fraction)

n  –  number of records the proportion is based on (count)

z  –  standard normal quantile for 95 % confidence, 1.96

For macro-F1 and for differences between methods, a stratified percentile bootstrap is used (Efron and Tibshirani, 1993):

CI95boot=ψ0.025*,  ψ0.975*#22

where:

ψ*  –  value of the measure (for example macro-F1, or the difference between two methods) computed on one bootstrap resample

ψ0.025*,  ψ0.975*  –  the 2.5th and 97.5th percentiles of the B bootstrap values

B  –  number of bootstrap resamples, 2000; each resample draws records with replacement within each class

For cross-validation results, the mean and standard deviation over the 50 outer estimates are reported.

## 6.3 Describing the gases by class

Gas values per class are summarised by the median and the interquartile range. Whether a gas differs between classes is tested with the Kruskal-Wallis test (Kruskal and Wallis, 1952), with rank epsilon-squared as the effect size:

H=12nn+1c=1KRc2nc-3n+1#23

where:

H  –  Kruskal-Wallis statistic, compared with a χ2 distribution with K-1 degrees of freedom (a correction for tied values is applied)

n  –  total number of records (count)

K  –  number of classes (count)

Rc  –  sum of the ranks of the records of class c when all records are ranked together by the gas value

nc  –  number of records in class c (count)

εR2=Hn+1n2-1#24

where:

εR2  –  rank epsilon-squared: the share of the rank variation explained by the class (0 to 1)

H and n are as defined under Equation (23).

How strongly pairs of gases rise and fall together (Figure 4.3) is measured with Spearman's rank correlation (Spearman, 1904):

ρs=i=1nui-uvi-vi=1nui-u2i=1nvi-v2#25

where:

ρs  –  Spearman rank correlation between two gases (from −1 to 1)

ui,  vi  –  ranks of record i for the first and for the second gas (tied values receive their average rank)

u,  v  –  mean of the ranks of each gas

n  –  number of records (count)

# 7. Statistical tests

Significance level: 0.05, two-sided, for every test. Exact p-values and effect sizes are always reported. A non-significant result is reported as no evidence of a difference, never as proof that two methods are equal.

## 7.1 Comparing the classifiers (cross-validation)

The Friedman test ranks the models within each outer fold (rank 1 = best macro-F1) and tests whether their average ranks differ (Friedman, 1937; Demšar, 2006):

χF2=12nfkk+1j=1kRj2-kk+124#26

where:

χF2  –  Friedman statistic, compared with a χ2 distribution with k-1 degrees of freedom

nf  –  number of outer folds over which the models are ranked, 50 (count)

k  –  number of models compared (count)

Rj  –  average rank of model j over the nf folds (1 = best)

If it is significant, the Nemenyi post-hoc test (Nemenyi, 1963) declares two models different when their average ranks differ by more than the critical difference:

CD=qαkk+16nf#27

where:

CD  –  critical difference: the smallest gap in average rank that counts as significant

qα  –  critical value of the Studentised range statistic divided by 2, for k models at α=0.05 (tabulated in Demšar, 2006)

k and nf are as defined under Equation (26).

Because cross-validation folds share training data, they are not fully independent. For the key pairwise comparison (the best model against the next), the corrected resampled t-test is therefore also reported (Nadeau and Bengio, 2003):

t=d1k r+ntestntrainσd2#28

where:

t  –  corrected resampled t statistic, compared with a t distribution with kr-1 degrees of freedom

d  –  mean, over all folds, of the difference in macro-F1 between the two models

σd2  –  variance of those fold-wise differences

k  –  number of folds per repeat, 5

r  –  number of repeats, 10

ntest,  ntrain  –  number of records in the test part and in the training part of one fold (count)

## 7.2 Omnibus test across all methods: Cochran's Q

On one test set, each method is either right or wrong on each record. Cochran's Q (Cochran, 1950) tests whether all methods have the same proportion correct. ND counts as wrong.

Q=m-1mj=1mCj2-T2mT-i=1Nai2#29

where:

Q  –  Cochran's Q statistic, compared with a χ2 distribution with m-1 degrees of freedom

m  –  number of methods compared: 4 (the ML model, Rogers, IEC 60599 and Duval)

Cj  –  number of records method j diagnosed correctly (count)

ai  –  number of methods that diagnosed record i correctly (0 to m)

T  –  total number of correct diagnoses over all methods, T=jCj

N  –  number of test records (count)

## 7.3 Pairwise test: ML against each conventional method (McNemar)

For two methods on the same records, only the records on which they differ carry information (McNemar, 1947):

χ2=b-c-12b+c#30

where:

χ2  –  McNemar statistic with continuity correction, compared with a χ2 distribution with 1 degree of freedom

b  –  number of records the ML model got right and the conventional method got wrong (count)

c  –  number of records the conventional method got right and the ML model got wrong (count)

When b+c<25, the exact binomial version is used instead:

p=min1,  2i=0minb,cb+ci0.5b+c#31

where:

p  –  exact two-sided p-value

i  –  summation index

b+ci  –  binomial coefficient: the number of ways to choose i of the b+c discordant records

0.5  –  probability of each kind of discordant record if the two methods are equally accurate

The effect size is the odds ratio bc, with its 95 % confidence interval.

## 7.4 Correction for multiple comparisons (Holm)

Three pairwise McNemar tests are run on each test set (ML against Rogers, IEC 60599 and Duval). The Holm procedure (Holm, 1979) keeps the chance of any false positive at 0.05: the p-values are ordered from smallest to largest and each hypothesis, in that order, is rejected while

pi≤αm-i+1#32

where:

pi  –  the i-th smallest of the p-values in the family

α  –  family-wise significance level, 0.05

m  –  number of tests in the family, 3 per test set

i  –  rank of the p-value (1 = smallest)

Testing stops at the first p-value that fails the condition.

## 7.5 Agreement between methods (Cohen's kappa)

Cohen's kappa (Equation 19; Cohen, 1960) is computed between every pair of methods, including the ML model, giving an agreement matrix (Table 4.7, Figure 4.11). Verbal labels for kappa values are used only as a guide, never as a test.

## 7.6 Is disagreement concentrated near the boundaries? (logistic regression)

For each conventional method, every test record is marked as a disagreement case or not, and the probability of disagreement is modelled against the record's distance to the nearest boundary (Section 4.5):

lnπi1-πi=β0+β1di#33

where:

πi  –  probability that test record i is a disagreement case, πi=PDi=1

Di  –  disagreement indicator of record i: 1 if the ML and the conventional diagnosis differ, 0 otherwise

di  –  boundary distance of record i (Equation 9 or 10), standardised to a z-score

β0  –  intercept: the log-odds of disagreement at the average distance

β1  –  slope: the change in the log-odds of disagreement for one standard deviation more distance

ln  –  natural logarithm

OR=eβ1  95% CI=eβ1±1.96 SEβ1#34

where:

OR  –  odds ratio of disagreement per standard deviation of distance

e  –  base of the natural logarithm (about 2.718)

SEβ1  –  standard error of β1 from the fitted model

1.96  –  standard normal quantile for 95 % confidence

In simple words: the odds ratio tells how the chance of disagreement changes when a sample is one standard deviation further from the nearest chart line. The hypothesis expects β1<0. Records for which no distance can be computed (a needed gas is missing) are excluded from this model and counted. If the fit shows complete separation, Firth's penalised logistic regression (Firth, 1993) is used.

# 8. Reduced-gas study

With five gases, the number of non-empty gas subsets is

25-1=31#35

where:

25  –  number of ways to include or leave out each of the five gases (32), from which the empty subset is subtracted

The ML pipeline is retrained and re-evaluated for every subset on the same folds as the full panel; only the available gases change, and a ratio feature is used only when both of its gases are present. For each subset the loss is

ΔS=Macro-F1full-Macro-F1S#36

where:

ΔS  –  loss of macro-F1 when only the gases in subset S are available (fraction; a positive value means worse)

S  –  a subset of the five gases

Macro-F1full  –  macro-F1 of the pipeline with all five gases

Macro-F1S  –  macro-F1 of the same pipeline, on the same folds, with only the gases in S

The minimum panel is the subset with the fewest gases whose loss satisfies

U95ΔS≤δ#37

where:

U95ΔS  –  upper limit of the 95 % bootstrap confidence interval of ΔS

δ  –  largest acceptable loss, fixed before the study (proposed 0.05, i.e. 5 percentage points of macro-F1; for approval)

For the conventional methods, applicability follows directly from their formulas: the Rogers and IEC 60599 ratios need all five gases, and Duval Triangle 1 needs CH4, C2H4 and C2H2; if any of these is missing the method gives ND.

## 8.1 Which gases matter most (explainability)

Permutation importance (Breiman, 2001) measures how much the score drops when the values of one feature are randomly shuffled:

Ij=s-1Rr=1Rsr,j#38

where:

Ij  –  permutation importance of feature j (fraction of macro-F1)

s  –  macro-F1 of the fitted model on the original test data

sr,j  –  macro-F1 after the values of feature j are randomly shuffled, in repeat r

R  –  number of shuffle repeats (proposed 30)

SHAP values (Lundberg and Lee, 2017) split each prediction into contributions of the individual features; the overall importance of a feature is the mean absolute contribution:

Φj=1Ni=1Nφi,j#39

where:

Φj  –  overall SHAP importance of feature j, in the units of the model output

φi,j  –  SHAP value: the contribution of feature j to the model output for record i

N  –  number of records explained (count)

The ranking will be compared with engineering knowledge (for example, the link between acetylene and high-energy discharges) and reported as found, even where it differs.

# 9. Simulink operating-model results

The Simulink model provides the operating context only: load, temperatures and insulation ageing. It never produces gas values. Its equations are the IEC 60076-7 differential equations, implemented as described in the MATLAB Build Guide (Section A3.2), with the constants in params_transformer.m (a copy of IEC 60076-7 is still to be obtained; TO VERIFY against the standard).

## 9.1 Thermal equations

Top-oil temperature:

k11τo⋅dθodt=1+K2R1+RxΔθor-θo-θa#40

where:

θo  –  top-oil temperature [°C]

θa  –  ambient temperature [°C]

t  –  time [min]

k11  –  oil thermal-model constant, 0.5 (dimensionless)

τo  –  oil time constant, 150 min

K  –  load factor: load current divided by rated current [per unit]

R  –  ratio of the load losses at rated current to the no-load losses, 7.556 (dimensionless)

x  –  oil exponent, 0.8 (dimensionless)

Δθor  –  top-oil temperature rise above ambient at rated load, 60 K

Hot-spot temperature rise, calculated as the difference of two parts:

k21ΔθhrKy=k22τw⋅dΔθh1dt+Δθh1#41

where:

Δθh1  –  first component of the hot-spot-to-top-oil temperature gradient [K]

Δθhr  –  hot-spot-to-top-oil gradient at rated load [K], from Equation (43)

y  –  winding exponent, 1.3 (dimensionless)

k21,  k22  –  winding thermal-model constants, both 2 (dimensionless)

τw  –  winding time constant, 7 min

k21-1ΔθhrKy=τok22⋅dΔθh2dt+Δθh2#42

where:

Δθh2  –  second component of the hot-spot-to-top-oil temperature gradient [K]

All other symbols are as defined under Equations (40) and (41).

θh=θo+Δθh1-Δθh2  Δθhr=H⋅gr  R=PkP0#43

where:

θh  –  hot-spot (hottest winding) temperature [°C]

H  –  hot-spot factor, 1.3 (dimensionless)

gr  –  average winding-to-average-oil temperature gradient at rated current, 17 K

Pk  –  load (copper) losses at rated current, 136 kW

P0  –  no-load (core) losses, 18 kW

Source of the constants: Alliander transformer-thermal-model ONAF defaults, an implementation of IEC 60076-7 (as recorded in params_transformer.m).

## 9.2 Insulation ageing

V=2θh-986  L=t1t2Vdt#44

where:

V  –  relative ageing rate of the paper insulation (dimensionless; equal to 1 at a hot-spot temperature of 98 °C)

L  –  loss of life over the period, in equivalent hours at 98 °C [h]

t1,  t2  –  start and end of the period [h]

98  –  reference hot-spot temperature for normal Kraft paper [°C]

6  –  rise in hot-spot temperature that doubles the ageing rate [K]

Source of this form: IntechOpen chapter, Table 1, as recorded in params_transformer.m; to be checked against IEC 60076-7.

## 9.3 Verification measures

emax=maxtθsimt-θreft#45

where:

emax  –  largest absolute difference between the model and the reference [K]

θsimt  –  top-oil or hot-spot temperature from the Simulink model at time t [°C]

θreft  –  the same temperature from an independent numerical solution of Equations (40) to (43) [°C]

t  –  time, from 10 min after the start to the end of the run

RMSE=1Mm=1Mθsimtm-θreftm2#46

where:

RMSE  –  root-mean-square difference between model and reference [K]

M  –  number of compared time points (count)

tm  –  the m-th compared time point

Proposed acceptance criterion (for approval): emax≤0.1 K for both top-oil and hot-spot temperature, and a top-oil 63 % rise time equal to k11τo.

## 9.4 Baseline already obtained (3 October 2026)

The reference build has already been verified. The values below are copied from verification_log_2026-10-03.txt and will be re-confirmed in Steps 3 and 35 of the roadmap.

| Test | Quantity | Value |
| --- | --- | --- |
| Rated load (logged K = 0.9839; ambient 20 °C) | Final top-oil / hot-spot temperature | 78.638 / 100.276 °C |
| Rated load | Largest model-reference difference after 10 min | Top-oil 0.006 K; hot-spot 0.061 K |
| Rated load | Top-oil 63 % rise time | 75.0 min (expected 0.5 × 150 min = 75.0 min) |
| Load step (logged K 0.5960 to 1.1733) | Largest model-reference difference after 10 min | Top-oil 0.003 K; hot-spot 0.031 K |
| Load step | Final top-oil / hot-spot temperature | 95.50 / 122.70 °C |

The reference solution was computed with the same logged load factor K as the model.

## 9.5 Scenario results expected

For each approved scenario (proposed: constant rated load, a daily load cycle and a short overload), the expected outputs are the time plots of Figure 4.19; the peak hot-spot temperature and the time it occurs; and the loss of life L over the scenario. These describe the operating context shown on the dashboard; they are not used in the diagnosis benchmark.

# 10. Integration results

F=nmatchN#47

where:

F  –  fidelity of the integrated system (fraction; required value 1)

nmatch  –  number of held-out records for which the service returns exactly the same class as the offline analysis (count)

N  –  number of held-out records sent to the service (count)

Requirement: F = 1 (100 %); any mismatch is traced and fixed before results are written. Response time is reported as the median and the 95th percentile of the time between sending a request and receiving the answer, measured on the project laptop over all test records (Figure 4.21). Proposed target for interactive use (for approval): 95th-percentile response time below 1 second.

# 11. How each result will be interpreted

•  A method is called better than another only when the Holm-adjusted p-value is below 0.05 and the effect (accuracy difference or odds ratio) points the same way. The size of the difference is always given.

•  A non-significant result is reported as no evidence of a difference, with its confidence interval, which shows how large a difference cannot be ruled out.

•  Results on the IEC TC 10 benchmark are always shown next to the home-advantage caveat of Section 3.2.

•  Strict and conditional accuracy are always shown together with coverage, so that no method is judged only on the cases it chose to answer.

•  Negative or modest results are reported as found; no setting is changed after the test sets have been opened.

# 12. Expected result tables and figures

## 12.1 Result tables

The list below gives every Chapter 4 table. The three templates that follow show the form of the main results. They are empty on purpose: the cells marked [ ] will be filled only by the analysis scripts, and nothing will be typed by hand.

•  Table 4.1 Data after cleaning: records per source, role and class, with exclusions.

•  Table 4.2 Gas medians and interquartile ranges per class, with Kruskal-Wallis H, p and epsilon-squared.

•  Table 4.3 Conventional methods on each test set: strict and conditional accuracy, coverage, ND and DT counts.

•  Table 4.4 Classifier cross-validation results: macro-F1 and balanced accuracy (mean and SD), average Friedman rank.

•  Table 4.5 Main comparison on each test set (template below).

•  Table 4.6 Paired tests of ML against each conventional method (template below).

•  Table 4.7 Cohen's kappa between all pairs of methods.

•  Table 4.8 Logistic regression of disagreement on boundary distance: coefficient, odds ratio, 95 % CI, p.

•  Table 4.9 Reduced-gas results (template below).

•  Table 4.10 Simulink verification (baseline in Section 9.4).

•  Table 4.11 Integration fidelity and response time.

Table 4.5 (template) - Main comparison on the IEC TC 10 benchmark (repeated for the internal and external test sets)

| Method | Strict accuracy (95 % CI) | Conditional accuracy (95 % CI) | Coverage (95 % CI) | Macro-F1 (95 % CI) |
| --- | --- | --- | --- | --- |
| ML (selected model) | [ ] | [ ] | [ ] | [ ] |
| Rogers Ratio | [ ] | [ ] | [ ] | [ ] |
| IEC 60599 ratio | [ ] | [ ] | [ ] | [ ] |
| Duval Triangle 1 | [ ] | [ ] | [ ] | [ ] |

Table 4.6 (template) - ML against each conventional method (McNemar, Holm-adjusted)

| Comparison | b | c | Statistic | p | p (Holm) | Odds ratio b/c (95 % CI) |
| --- | --- | --- | --- | --- | --- | --- |
| ML vs Rogers Ratio | [ ] | [ ] | [ ] | [ ] | [ ] | [ ] |
| ML vs IEC 60599 ratio | [ ] | [ ] | [ ] | [ ] | [ ] | [ ] |
| ML vs Duval Triangle 1 | [ ] | [ ] | [ ] | [ ] | [ ] | [ ] |

Table 4.9 (template) - Reduced-gas study

| Gas subset | Number of gases | ML macro-F1 (95 % CI) | Loss (95 % CI) | Within tolerance? | Conventional methods still usable |
| --- | --- | --- | --- | --- | --- |
| All five gases | 5 | [ ] | 0 (reference) | - | Rogers, IEC 60599, Duval |
| Without C2H6 | 4 | [ ] | [ ] | [ ] | Duval only |
| Without H2 | 4 | [ ] | [ ] | [ ] | Duval only |
| H2 only | 1 | [ ] | [ ] | [ ] | None |
| ... (all 31 subsets) |  |  |  |  |  |

The last column of Table 4.9 is not a result: it follows directly from which gases each conventional method needs (Section 8).

## 12.2 Rules that apply to every figure

•  Every figure is drawn by a script, never by hand. The numbers plotted are saved as a CSV file with the same name beside the figure in 11_Results/figures; that file is the table view of the figure and lets any value be checked.

•  Each figure is saved twice: PNG at 300 dpi for the Word thesis, and PDF (vector) for the journal. Width is 16 cm (full page) or 8 cm (half page).

•  Lettering is a plain sans-serif (Arial) at 9-10 pt at final size. Every axis carries a label and its unit in square brackets.

•  One vertical axis per plot - never two different y-scales on the same chart. Quantities with different units are drawn in separate panels that share the horizontal axis.

•  Fixed colours (table below): each fault class and each method keeps the same colour in every figure, in both environments. Python and MATLAB read the colours and marker shapes from one shared file, 11_Results/figures/plot_style.csv, so figures from Claude Code and from the MATLAB and Simulink toolkits match.

•  A figure is coloured either by fault class or by method, never both at once, and a legend always names the colours. In scatter plots each class also has its own marker shape, so colour is never the only clue (important for colour-blind readers and for black-and-white printing).

•  Magnitudes on heatmaps use one hue from light to dark; quantities that can be negative (kappa, correlation) use a two-colour scale (blue for positive, red for negative) with grey at zero. No rainbow scales, no 3-D effects, no pie charts.

•  Gas concentrations and the ageing rate are shown on logarithmic axes, and the axis label says so.

•  Error bars and shaded bands are always 95 % confidence intervals computed as in Section 6.2, and the caption says so. Every caption also gives the data set and the number of records n.

•  Thin lines, light solid gridlines, and values written on the chart only where they help (for example the counts in a confusion matrix).

Fixed colours and marker shapes (stored in plot_style.csv)

| Used for | Item | Colour (hex) | Marker shape |
| --- | --- | --- | --- |
| Fault class | Normal | Grey #898781 | Circle |
| Fault class | PD - partial discharge | Blue #2A78D6 | Square |
| Fault class | D1 - low-energy discharge | Orange #EB6834 | Triangle (up) |
| Fault class | D2 - high-energy discharge | Aqua #1BAF7A | Diamond |
| Fault class | T1 - thermal below 300 °C | Yellow #EDA100 | Triangle (down) |
| Fault class | T2 - thermal 300 to 700 °C | Magenta #E87BA4 | Pentagon |
| Fault class | T3 - thermal above 700 °C | Green #008300 | Hexagon |
| Fault class | T1/T2 merged (IEC TC 10 only) | Violet #4A3AA7 | Cross |
| Method | ML (selected model) | Blue #2A78D6 | Circle |
| Method | Rogers Ratio | Orange #EB6834 | Square |
| Method | IEC 60599 ratio | Aqua #1BAF7A | Diamond |
| Method | Duval Triangle 1 | Yellow #EDA100 | Triangle (up) |

The colours are taken unchanged, in their fixed order, from a palette whose order has been checked for colour-blind safety; Normal is grey because it means no fault.

## 12.3 List of figures

| No. | Figure | Chart type | Made in | Step |
| --- | --- | --- | --- | --- |
| 3.1 | The integrated framework | Block diagram | Claude Code | 43 |
| 3.2 | Data-preparation flow with record counts | Flow chart | Claude Code | 13 |
| 3.3 | Nested cross-validation scheme | Schematic | Claude Code | 43 |
| 3.4 | Simulink operating model, top level | Model screenshot | Simulink toolkit | 33 |
| 4.1 | Records per fault class | Bar chart, 4 panels | Claude Code | 11 |
| 4.2 | Gas concentrations by fault class | Box plots, 5 panels, log scale | Claude Code | 11 |
| 4.3 | Correlation between gases | Heatmap | Claude Code | 11 |
| 4.4 | Duval Triangle with the samples | Triangle (ternary) scatter | MATLAB toolkit | 17 |
| 4.5 | Confusion matrices of the conventional methods | Heatmaps | Claude Code | 29 |
| 4.6 | Cross-validation performance of the classifiers | Box plot with points | Claude Code | 32 |
| 4.7 | Critical-difference diagram | Rank diagram | Claude Code | 30 |
| 4.8 | Confusion matrices of the ML model | Heatmaps | Claude Code | 29 |
| 4.9 | ML versus conventional: main comparison | Dot-and-whisker, 3 panels | Claude Code | 32 |
| 4.10 | F1-score per fault class | Grouped bars with CIs | Claude Code | 32 |
| 4.11 | Agreement between methods | Heatmap (kappa) | Claude Code | 30 |
| 4.12 | Disagreement against boundary distance | Logistic curve with binned points | Claude Code | 31 |
| 4.13 | Disagreements in the Duval Triangle | Triangle (ternary) scatter | Claude Code | 32 |
| 4.14 | Permutation importance | Horizontal bars with CIs | Claude Code | 23 |
| 4.15 | SHAP summary | Beeswarm plot | Claude Code | 23 |
| 4.16 | Accuracy against number of gases | Points and line with band | Claude Code | 27 |
| 4.17 | Gas-subset matrix | Dot matrix with bars | Claude Code | 27 |
| 4.18 | Verification of the Simulink thermal model | Line chart, 2 panels | Simulink toolkit | 35 |
| 4.19 | Operating scenarios | Line chart, 3 panels | Simulink toolkit | 36 |
| 4.20 | Test-bench run | Line chart with event markers | MATLAB toolkit | 41 |
| 4.21 | Response time of the service | Histogram and cumulative curve | Claude Code | 42 |
| 4.22 | The dashboard | Annotated screenshot | MATLAB toolkit | 39 |

## 12.4 Each figure in detail

For every figure: the type of chart, what is on each axis, how colours and panels are used, the file the data come from, where it is made, and how to read it.

Figure 3.1  The integrated framework

Type: Block diagram (not a data graph), drawn as vector graphics.

Content: The three working environments (Claude Code, MATLAB toolkit, Simulink toolkit) as three columns; the hand-over files as labelled arrows between them; the four data sets on the left and the dashboard on the right.

Made in: [CLAUDE CODE]  Step 43.

How to read it: It shows how all parts connect, before any result is presented.

Figure 3.2  Data-preparation flow with record counts

Type: Flow chart of boxes and arrows.

Content: One box per stage: raw files (n per source), standardised, excluded by scope (n and reason), duplicates removed (n), final records per data role (n). The counts are filled in automatically from the logs of Steps 5 to 10.

Data: 03_Data/interim logs; dga_master.csv.

Made in: [CLAUDE CODE]  Step 13.

How to read it: Every record that is dropped is accounted for; the final boxes equal Table 4.1.

Figure 3.3  Nested cross-validation scheme

Type: Schematic.

Content: The development set cut into 5 outer folds, repeated 10 times; inside each outer training part, 5 inner folds used only for tuning; the three test sets kept aside until Step 22.

Made in: [CLAUDE CODE]  Step 43.

Figure 3.4  Simulink operating model, top level

Type: Model screenshot exported from Simulink.

Content: The seven subsystems SS1 to SS7 with their connections and annotations.

Made in: [SIMULINK AGENTIC TOOLKIT]  Step 33.

Figure 4.1  Records per fault class

Type: Bar chart in four panels (small multiples), one panel per data role.

Axes: Horizontal: fault class (Normal, PD, D1, D2, T1, T2, T3; T1/T2 merged in the IEC TC 10 panel). Vertical: number of records [count].

Colours: Each bar in its class colour; the count written above each bar.

Data: dga_master.csv.

Made in: [CLAUDE CODE]  Step 11 (Python, matplotlib).

How to read it: Shows how unbalanced the classes are and which are small - the reason for using macro-F1 and confidence intervals.

Figure 4.2  Gas concentrations by fault class

Type: Box plots in five panels, one per gas: the line is the median, the box the interquartile range, the whiskers reach 1.5 times that range, and single points are outliers.

Axes: Horizontal: fault class. Vertical: gas concentration [ppm], logarithmic scale.

Colours: Boxes in class colours. Each panel title gives the Kruskal-Wallis H, p and epsilon-squared (Equations 23 and 24).

Data: dga_master.csv, development set (a benchmark version goes to the appendix).

Made in: [CLAUDE CODE]  Step 11.

How to read it: Shows which gases separate which faults - for example whether acetylene is high mainly in the discharge classes.

Figure 4.3  Correlation between gases

Type: Heatmap, 5 x 5.

Axes: The five gases on both axes.

Colours: Two-colour scale from -1 (red) through 0 (grey) to +1 (blue); the Spearman coefficient (Equation 25) written in each cell.

Data: dga_master.csv, development set.

Made in: [CLAUDE CODE]  Step 11.

How to read it: Strongly correlated gases carry overlapping information, which helps explain the reduced-gas results.

Figure 4.4  Duval Triangle with the samples

Type: Triangle (ternary) scatter plot.

Axes: The three sides give %CH4, %C2H4 and %C2H2 from 0 to 100 %, with ticks every 10 %.

Marks: Each sample is a point at its coordinates (Equation 5), coloured and shaped by its true class; zone outlines from duval_triangle_zones.csv as thin grey lines with zone labels (PD, D1, D2, T1, T2, T3, DT).

Panels: One triangle per data role.

Made in: [MATLAB AGENTIC TOOLKIT]  Step 17 (plot_duval_triangle.m).

How to read it: A point lying in the zone of its own class is a correct Duval diagnosis; points close to zone lines are the borderline cases studied in RQ2.

Figure 4.5  Confusion matrices of the conventional methods

Type: Heatmaps (confusion matrices).

Axes: Rows: true class. Columns: class given by the method, plus an ND column (and a DT column for Duval).

Colours: Single blue scale for the row percentage (white = 0 %, dark blue = 100 %); each cell shows the count and the row percentage.

Panels: Rogers, IEC 60599, Duval; one figure per test set.

Data: merged_predictions.csv.

Made in: [CLAUDE CODE]  Step 29.

How to read it: The diagonal holds the correct answers; the ND column shows, class by class, how often each method gives no answer.

Figure 4.6  Cross-validation performance of the classifiers

Type: Box plot with the 50 individual fold values overlaid as small dots.

Axes: Horizontal: model (baseline, SVM, Random Forest, XGBoost, MLP, fifth model). Vertical: macro-F1 (0 to 1).

Colours: One colour for all models (blue); the baseline in grey.

Data: 07_Experiments fold results.

Made in: [CLAUDE CODE]  Step 32 (results from Step 20).

How to read it: Height shows how good a model is; spread shows how stable it is from fold to fold.

Figure 4.7  Critical-difference diagram

Type: Rank diagram (Demšar, 2006).

Axis: Average rank (1 = best) on one horizontal scale.

Marks: Each model is a tick with its name; a thick bar joins models whose average ranks differ by less than the critical difference (Equation 27); the CD length is drawn above the axis.

Made in: [CLAUDE CODE]  Step 30.

How to read it: Models joined by a bar cannot be told apart statistically.

Figure 4.8  Confusion matrices of the ML model

Type: Heatmaps, same design as Figure 4.5 (no ND column, because the ML model always answers).

Panels: Internal test set; IEC TC 10 benchmark (five merged classes); Li 2019.

Made in: [CLAUDE CODE]  Step 29.

How to read it: Shows which faults the ML model confuses with each other.

Figure 4.9  ML versus conventional methods: main comparison

Type: Dot-and-whisker plot: a dot for the estimate and a horizontal bar for its 95 % confidence interval.

Axes: Vertical: method (ML, Rogers, IEC 60599, Duval). Horizontal: value of the measure (0 to 1).

Panels: Three panels side by side sharing the vertical axis: strict accuracy, conditional accuracy, macro-F1; coverage written beside each method name. One figure per test set.

Colours: Method colours.

Made in: [CLAUDE CODE]  Step 32.

How to read it: Clearly separated bars suggest a real difference (the formal test is in Table 4.6). The gap between the strict and the conditional panel shows how much the no-diagnosis cases cost each method - criterion 2 of the hypothesis.

Figure 4.10  F1-score per fault class

Type: Grouped bar chart with 95 % confidence-interval bars.

Axes: Horizontal: fault class. Vertical: F1-score (0 to 1).

Colours: One bar per method in the method colours; legend above the plot.

Made in: [CLAUDE CODE]  Step 32.

How to read it: Shows which faults each method diagnoses well or badly, for example whether D1 and D2 are confused.

Figure 4.11  Agreement between methods

Type: Heatmap of Cohen's kappa, 5 x 5 (the four methods plus the true label).

Colours: Two-colour scale from -1 (red) through 0 (grey) to +1 (blue); the kappa value in each cell.

Made in: [CLAUDE CODE]  Step 30.

How to read it: A high value means two methods usually give the same answer.

Figure 4.12  Disagreement against distance to the boundary

Type: Fitted logistic curve with observed rates.

Axes: Horizontal: standardised boundary distance (z-score). Vertical: probability of disagreement (0 to 1).

Marks: The fitted curve of Equation 33 with a shaded 95 % band; the observed disagreement rate in ten equal-sized distance groups as points with Wilson 95 % bars (Equation 21); short ticks along the bottom (agree) and top (disagree) for the individual records.

Panels: Rogers, IEC 60599, Duval.

Made in: [CLAUDE CODE]  Step 31.

How to read it: A curve that falls from left to right supports the boundary hypothesis; a flat curve does not.

Figure 4.13  Disagreements in the Duval Triangle

Type: Triangle (ternary) scatter, as Figure 4.4.

Marks: Records where the ML model and Duval agree as small grey points; records where they disagree as larger points in class colour and shape.

Made in: [CLAUDE CODE]  Step 32 (same zone file and coordinates as duval_xy.m, so it matches the MATLAB figure).

How to read it: If the disagreements cluster along the zone lines, the boundary hypothesis can be seen directly.

Figure 4.14  Permutation importance

Type: Horizontal bar chart with 95 % interval bars over the shuffle repeats.

Axes: Vertical: feature, most important at the top. Horizontal: drop in macro-F1 (Equation 38).

Colours: One colour.

Made in: [CLAUDE CODE]  Step 23.

How to read it: A long bar means the model relies heavily on that feature.

Figure 4.15  SHAP summary

Type: Beeswarm plot: one point per record and feature.

Axes: Vertical: features ranked by mean absolute SHAP value (Equation 39). Horizontal: SHAP value (contribution to the model output).

Colours: Point colour shows the feature's own value on a single blue scale (light = low, dark = high).

Panels: One panel per fault class.

Made in: [CLAUDE CODE]  Step 23.

How to read it: Points far to the right push the model towards that class; the colour shows whether high or low gas values do the pushing.

Figure 4.16  Accuracy against number of gases

Type: Points with a line and shaded band.

Axes: Horizontal: number of gases available (1 to 5). Vertical: macro-F1 (0 to 1).

Marks: Each of the 31 subsets as a small grey point; the best subset of each size joined by a line with its 95 % band; a horizontal reference line at the full-panel macro-F1 minus the tolerance; the minimum panel (Equation 37) labelled with its gases.

Made in: [CLAUDE CODE]  Step 27.

How to read it: The smallest number of gases whose best subset stays above the reference line gives the minimum useful panel.

Figure 4.17  Gas-subset matrix

Type: Dot matrix with bars (UpSet-style layout).

Content: Lower part: one column per gas subset and one row per gas, with a filled dot where the gas is included. Upper part: the ML macro-F1 of each subset as a bar with its 95 % interval, columns ordered from best to worst. Bottom rows: a tick where Rogers, IEC 60599 or Duval can still be used.

Made in: [CLAUDE CODE]  Step 27.

How to read it: Shows at a glance which gas combinations still work and which conventional methods would be lost.

Figure 4.18  Verification of the Simulink thermal model

Type: Line chart in two panels sharing the time axis.

Axes: Horizontal: time [h]. Upper panel: temperature [°C] - top-oil and hot-spot from the model (solid) and from the reference solution (dashed). Lower panel: model minus reference [K].

Panels: Rated-load test and load-step test.

Data: Simulation Data Inspector logs; reference solution from the verification script.

Made in: [SIMULINK AGENTIC TOOLKIT]  Step 35 (plotted in MATLAB). The 3 October version exists as reference_build/figures/fig_verification.png.

How to read it: Curves lying on top of each other, and a difference curve inside the approved tolerance, confirm the model.

Figure 4.19  Operating scenarios

Type: Line chart in three panels sharing the time axis (0 to 24 h); one figure per scenario.

Axes: Panel 1: load factor K [per unit]. Panel 2: ambient, top-oil and hot-spot temperatures [°C]. Panel 3: ageing rate V, logarithmic scale, with the loss of life L written at the end of the curve.

Made in: [SIMULINK AGENTIC TOOLKIT]  Step 36.

How to read it: Shows how the transformer heats and ages under each load pattern - the operating context for the diagnoses.

Figure 4.20  Test-bench run

Type: Line chart with event markers.

Axes: Horizontal: simulated time [h]. Vertical: hot-spot temperature [°C].

Marks: The hot-spot curve from the model; a marker at each DGA sampling event, coloured and shaped by the ML diagnosis, filled when ML and the conventional methods agree and hollow when they disagree.

Made in: [MATLAB AGENTIC TOOLKIT]  Step 41.

How to read it: Demonstrates the integrated system: real gas records diagnosed while the operating model runs.

Figure 4.21  Response time of the service

Type: Histogram in one panel and the cumulative curve in a second panel.

Axes: Horizontal: response time [ms]. Vertical: number of requests (histogram); cumulative share of requests, 0 to 1 (second panel).

Marks: Vertical lines at the median and at the 95th percentile, labelled with their values.

Made in: [CLAUDE CODE]  Step 42.

How to read it: The 95th-percentile line must lie to the left of the approved target.

Figure 4.22  The dashboard

Type: Annotated screenshot.

Content: The dashboard during a test-bench run, with numbered call-outs: gas values, the three conventional diagnoses, the ML diagnosis and its class probabilities, the Duval point, the agreement flag and the operating context.

Made in: [MATLAB AGENTIC TOOLKIT]  Step 39.

# 13. Quality and reproducibility safeguards

•  The data are frozen (version 1.0) with SHA-256 hashes before any model is trained.

•  All preprocessing is fitted inside the training folds; automated tests check for leakage.

•  Each test set is opened once, after the final model is chosen, and this is logged.

•  Fixed random seeds are saved with every experiment; every number traces to a file in 07_Experiments or 11_Results.

•  The conventional methods are implemented twice (MATLAB and Python) and must agree on 100 % of records.

•  Standards tables are transcribed twice and spot-checked by the student against the standard.

•  All tables and figures are produced by script; none is edited by hand, and every figure has its data saved beside it.

•  Anything not yet checked is marked TO VERIFY until it is closed.

# 14. Items for approval

Please mark each item as approved, or write the change wanted. Approving this list is Step 4 of the roadmap; nothing in Steps 5 to 32 starts before it.

| No. | Item | Proposed choice | Approved (Y/N) | Comment |
| --- | --- | --- | --- | --- |
| 1 | Primary performance measure | Macro-F1 |  |  |
| 2 | Main benchmark | IEC TC 10 (inspection-confirmed), scored on five merged classes |  |  |
| 3 | Data roles | Dissanayake train = development; Dissanayake unseen = internal test; Li 2019 = sensitivity only |  |  |
| 4 | Missing values | Primary: complete records only. Sensitivity: missing = 0 ppm |  |  |
| 5 | Normal class (D3) | Kept as class 0 where present; normality gate for the conventional methods |  |  |
| 6 | T1/T2 in IEC TC 10 | Scored as one merged T1/T2 class |  |  |
| 7 | Li 2019 label mapping | Partial discharge to PD; spark discharge to D1; arc discharge to D2; low-temperature overheating to T1; middle-temperature to T2; high-temperature to T3; low/middle-temperature to merged T1/T2 |  |  |
| 8 | Equipment scope (IEC TC 10) | Power transformers only (P, U); other types in a sensitivity analysis |  |  |
| 9 | Classifiers (D6) | SVM, Random Forest, XGBoost, MLP and a fifth model; majority-class baseline |  |  |
| 10 | Validation | Nested CV: outer 5-fold x 10 repeats; inner 5-fold; tuning on macro-F1 |  |  |
| 11 | Significance | 0.05, two-sided; Holm correction |  |  |
| 12 | Confidence intervals | Wilson for proportions; stratified bootstrap, B = 2000 |  |  |
| 13 | Reduced-gas tolerance | δ = 0.05 (macro-F1) |  |  |
| 14 | Simulink verification tolerance | Largest model-reference difference ≤ 0.1 K |  |  |
| 15 | Service requirements | Fidelity 100 %; 95th-percentile response time below 1 s |  |  |
| 16 | Gases (D2) | Five gases: H2, CH4, C2H6, C2H4, C2H2; CO and CO2 not used |  |  |
| 17 | Duval DT zone | A DT result counts as a diagnosis but as wrong; DT counts reported separately |  |  |
| 18 | Figures | The 26 figures of Section 12.3 with the colour and style rules of Section 12.2 |  |  |

# 15. References

Each reference will be checked against the original and logged in the project's reference register before it is used in the thesis (project rule).

Breiman, L. (2001). Random forests. Machine Learning, 45(1), 5-32.

Chawla, N. V., Bowyer, K. W., Hall, L. O., and Kegelmeyer, W. P. (2002). SMOTE: Synthetic minority over-sampling technique. Journal of Artificial Intelligence Research, 16, 321-357.

Cochran, W. G. (1950). The comparison of percentages in matched samples. Biometrika, 37(3/4), 256-266.

Cohen, J. (1960). A coefficient of agreement for nominal scales. Educational and Psychological Measurement, 20(1), 37-46.

Demšar, J. (2006). Statistical comparisons of classifiers over multiple data sets. Journal of Machine Learning Research, 7, 1-30.

Duval, M., and dePablo, A. (2001). Interpretation of gas-in-oil analysis using new IEC publication 60599 and IEC TC 10 databases. IEEE Electrical Insulation Magazine, 17(2), 31-41.

Efron, B., and Tibshirani, R. J. (1993). An Introduction to the Bootstrap. Chapman and Hall.

Firth, D. (1993). Bias reduction of maximum likelihood estimates. Biometrika, 80(1), 27-38.

Friedman, M. (1937). The use of ranks to avoid the assumption of normality implicit in the analysis of variance. Journal of the American Statistical Association, 32(200), 675-701.

Gorodkin, J. (2004). Comparing two K-category assignments by a K-category correlation coefficient. Computational Biology and Chemistry, 28(5-6), 367-374.

Holm, S. (1979). A simple sequentially rejective multiple test procedure. Scandinavian Journal of Statistics, 6(2), 65-70.

IEC 60076-7. Power transformers - Part 7: Loading guide for mineral-oil-immersed power transformers. (Edition to be confirmed - TO VERIFY.)

IEC 60599. Mineral oil-filled electrical equipment in service - Guidance on the interpretation of dissolved and free gases analysis. (Edition to be confirmed - TO VERIFY.)

IEEE Std C57.104-2019. IEEE Guide for the Interpretation of Gases Generated in Mineral Oil-Immersed Transformers.

Kruskal, W. H., and Wallis, W. A. (1952). Use of ranks in one-criterion variance analysis. Journal of the American Statistical Association, 47(260), 583-621.

Lundberg, S. M., and Lee, S.-I. (2017). A unified approach to interpreting model predictions. Advances in Neural Information Processing Systems, 30.

McNemar, Q. (1947). Note on the sampling error of the difference between correlated proportions or percentages. Psychometrika, 12(2), 153-157.

Nadeau, C., and Bengio, Y. (2003). Inference for the generalization error. Machine Learning, 52(3), 239-281.

Nemenyi, P. B. (1963). Distribution-free multiple comparisons. PhD thesis, Princeton University.

Spearman, C. (1904). The proof and measurement of association between two things. American Journal of Psychology, 15(1), 72-101.

Varma, S., and Simon, R. (2006). Bias in error estimation when using cross-validation for model selection. BMC Bioinformatics, 7, 91.

Wilson, E. B. (1927). Probable inference, the law of succession, and statistical inference. Journal of the American Statistical Association, 22(158), 209-212.