UNIVERSITY OF MINES AND TECHNOLOGY, TARKWA

Department of Electrical and Electronic Engineering

MATLAB BUILD GUIDE

MATLAB Code, Simulink–Simscape Transformer Model and Diagnostic App (MATLAB R2025b)

Project: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning

Step-by-step procedure, verified by building and simulating the model in MATLAB R2025b

Version 1.0 — 3 October 2026

TABLE OF CONTENTS

1. How to Use This Guide	4

1.1 What the finished MATLAB side does	4

1.2 How the three parts connect	5

2. Before You Start	5

2.1 Software (checked on the project computer)	5

2.2 Files and folders	6

2.3 Naming and annotation rules	6

PART A — MATLAB Code (.m Files)	7

A1. Project set-up	7

A2. The parameter file: params_transformer.m	7

A3. How the derived values are obtained	8

A4. Sources of the parameter values	9

A5. Room for the standards: what to replace when they arrive	10

A6. Supporting functions (provided and tested)	10

PART B — Simulink and Simscape Transformer Model	12

B1. Model layout	12

B2. Create the model and set it up	13

B3. Common procedures used in every subsystem	13

B4. SS1_Grid_Supply — the 110 kV supply	14

B5. SS2_Power_Transformer — the 40 MVA transformer	14

B6. SS3_LV_Measurement — current and load factor	16

B7. SS4_Variable_Load — the customer load	17

B8. SS5_Losses_to_Heat — from load factor to heat inputs	18

B9. SS6_Thermal_Network — oil and hot-spot thermal circuits	19

B10. SS7_Outputs_and_Ageing — results to the workspace	22

B11. Top-level connections	22

B12. Run and verify	23

B13. Errors met during verification and how to fix them	24

PART C — MATLAB App (App Designer Dashboard)	25

C1. Create the app	25

C2. Components	25

C3. Properties	26

C4. Callbacks	26

C5. Test the app	28

C6. Connecting the machine-learning service later (Phase 7)	28

PART D — Final Checklist and References	28

D1. Checklist before the work is accepted	28

D2. References used in this guide	29

# 1. How to Use This Guide

This guide tells the team exactly how to build the MATLAB side of the project in MATLAB R2025b. It has three parts, built in this order:

- Part A — MATLAB code (.m files): the parameter file and the small functions the model and the app call.

- Part B — Simulink and Simscape model: the transformer operating model, built subsystem by subsystem from Simscape physical blocks.

- Part C — MATLAB App (App Designer): the dashboard that runs the model, reads a measured DGA record and shows the diagnoses.

We checked every block, port, connection, and parameter in Part B against the installed MATLAB R2025b libraries. A script then built the complete model from these instructions and simulated it. Its temperatures agree with an independent solution of the IEC 60076-7 thermal equations to within 0.06 K (Section B11). The same check was made for every function in Part A and for the app in Part C.

Three rules that apply to every step 1. No number is typed into a block. Every value lives in params_transformer.m; blocks use only variable names. To change a value, edit the .m file only. 2. Every subsystem gets an annotation saying what it does, its inputs, its outputs and its parameters. The exact text is given for each subsystem. 3. No gas values are simulated. The Simulink model produces operating behaviour (load, current, oil and hot-spot temperature). Gas values always come from real measured records.

## 1.1 What the finished MATLAB side does

- params_transformer.m defines every parameter with its unit and source.

- The Simulink model Transformer_Operating_Model.slx simulates a 40 MVA, 110/20 kV transformer feeding a load that follows a profile. It computes the load factor from the measured secondary current, the losses, and the top-oil and hot-spot temperatures (IEC 60076-7 thermal model), plus the insulation ageing rate.

- run_transformer_simulation.m runs the model and returns the results in one structure.

- The App reads a measured DGA record and computes the gas ratios. It shows the conventional diagnoses (once the thresholds from the standards are transcribed), the machine-learning diagnosis (once the Python service exists) and the simulated operating condition, side by side.

## 1.2 How the three parts connect

| Stage | Produces | Used by | How it is passed |
| --- | --- | --- | --- |
| A. params_transformer.m | All parameters as named variables | Simulink model (every block); app | Run by the model callbacks PreLoadFcn and InitFcn |
| B. Simulink model | K_pu, theta_oil_C, theta_hs_C, ageing_rate_V | run_transformer_simulation.m | To Workspace blocks inside SS7, returned in the simulation output |
| A. run_transformer_simulation.m | Struct with time and the four signals | App: Run simulation button | Function return value |
| Measured DGA file (03_Data) | One record: H2, CH4, C2H6, C2H4, C2H2 | load_dga_record.m, then the app | CSV/XLSX file |
| A. gas_ratios.m, conventional_diagnosis.m | Ratios, Duval %, three conventional diagnoses | App: Diagnose button | Function return value |
| A. ml_diagnose.m | ML diagnosis (placeholder until Phase 7) | App: Diagnose button | HTTP/JSON to FastAPI (switched off for now) |

# 2. Before You Start

## 2.1 Software (checked on the project computer)

| Product | Version found | Used for |
| --- | --- | --- |
| MATLAB | R2025b (25.2.0.2998904, General Release, 21 Aug 2025) | Code, app |
| Simulink | 25.2 | Model canvas, signal blocks |
| Simscape | 25.2 | Physical networks: thermal blocks, utilities |
| Simscape Electrical | 25.2 | Transformer, source, load, three-phase sensor |
| Statistics and Machine Learning Toolbox | 25.2 | Later analysis (not needed for this guide) |

Specialized Power Systems is not used. In the R2025b General Release, the Specialized Power Systems library (powergui, the older SPS blocks) is not available. MathWorks staff state on MATLAB Answers that it returns in R2025b Update 1. This guide uses only Simscape and Simscape Electrical blocks, so it does not depend on that library. Do not mix the two families in one model.

Important: free space on drive C: During verification the C: drive of the project computer had only about 90 MB free. With so little space MATLAB switched off all data recording (warning: "Due to low available disk space ... turning off recording of all data"), and the simulation returned empty results. Before building, free at least 10 GB on C: (empty the Recycle Bin, remove old downloads, run Windows Disk Cleanup). MATLAB keeps its temporary files on C: by default.

## 2.2 Files and folders

| File | Folder | Part | Status |
| --- | --- | --- | --- |
| project_setup.m | project root | A | Provided, tested |
| params_transformer.m | 05_Simulink_Model | A | Provided, tested |
| run_transformer_simulation.m | 05_Simulink_Model | A | Provided, tested |
| Transformer_Operating_Model.slx | 05_Simulink_Model | B | Team builds it with Part B |
| reference_build/build_transformer_model.m | 05_Simulink_Model | B | Script that builds the same model automatically, for checking your build |
| gas_ratios.m, duval_xy.m, conventional_diagnosis.m, plot_duval_triangle.m | 04_MATLAB_Conventional | A | Provided, tested; thresholds pending the standards |
| load_dga_record.m, ml_diagnose.m | 10_Dashboard_Client | A | Provided, tested |
| DGADashboard.mlapp | 10_Dashboard_Client | C | Team builds it with Part C |
| DGADashboard_reference.m | 10_Dashboard_Client | C | Same app written in code, tested, for comparison |

## 2.3 Naming and annotation rules

- Subsystems: SSn_Description (for example SS2_Power_Transformer). Blocks: descriptive names with underscores (Grid_Source, Thermal_Mass_Oil). Rename a block by clicking its name.

- Variables: units shown in the comment of params_transformer.m, for example [W], [K/W], [pu].

- To add an annotation: double-click an empty part of the canvas, type the text, click outside. Give it a light background (right-click > Format > Background Color). Put it at the bottom of each subsystem.

- Mathematical constants that are not parameters (1/3 in an RMS formula, log(2), 273.15 for kelvin) may appear in a block, because they are definitions, not data.

# PART A — MATLAB Code (.m Files)

## A1. Project set-up

Step A1.1 Open MATLAB R2025b. In the Current Folder panel, browse to the project folder.

Step A1.2 Run project_setup.m (type project_setup in the Command Window). It adds the three MATLAB folders to the path and loads the parameters. Run it at the start of every session.

%% project_setup.m % Run this once at the start of every MATLAB session (or add it to startup). % It puts all project MATLAB folders on the path and loads the parameters. root = fileparts(mfilename('fullpath')); addpath(fullfile(root, '04_MATLAB_Conventional')); addpath(fullfile(root, '05_Simulink_Model')); addpath(fullfile(root, '10_Dashboard_Client')); params_transformer; % parameters into the base workspace fprintf('Project paths added. Parameters loaded from params_transformer.m\n');

## A2. The parameter file: params_transformer.m

This file is the single source of every number used by the model. Each line has a unit and a source code (E1, T1) that points to the reference list in Section A4. Values marked T1 are to be replaced by IEC 60076-7 or test-report values when available (Section A5).

%% params_transformer.m % Parameters for the Simscape transformer operating model. % Every value has a unit and a source. Blocks in the model use ONLY these % variable names; no number is typed into a block dialog. %% 1. Electrical rating (Source E1: pandapower standard type "40 MVA 110/20 kV") S_rated = 40e6; % [VA] rated apparent power (E1: sn_mva = 40) V_HV = 110e3; % [V] primary rated line-to-line RMS voltage (E1: vn_hv_kv = 110) V_LV = 20e3; % [V] secondary rated line-to-line RMS voltage (E1: vn_lv_kv = 20) f_rated = 50; % [Hz] rated frequency (E1: standard types are for 50 Hz) uk_pct = 16.2; % [%] short-circuit impedance voltage (E1: vk_percent) ukr_pct = 0.34; % [%] resistive part of uk (E1: vkr_percent) P0 = 18e3; % [W] no-load (core) loss (E1: pfe_kw = 18) i0_pct = 0.05; % [%] no-load current (E1: i0_percent) phase_shift_deg = 0; % [deg] grid source phase angle (reference phasor, by definition 0) %% 2. Derived electrical quantities (standard per-unit relations; see guide Section A3) Pk = ukr_pct/100 * S_rated; % [W] load (copper) loss at rated current R_pu_tot = ukr_pct/100; % [pu] total series resistance X_pu_tot = sqrt(uk_pct^2 - ukr_pct^2)/100; % [pu] total leakage reactance Rw1_pu = R_pu_tot/2; Rw2_pu = R_pu_tot/2; % [pu] equal split between windings (assumption A1) Xl1_pu = X_pu_tot/2; Xl2_pu = X_pu_tot/2; % [pu] equal split between windings (assumption A1) Rm_pu = S_rated/P0; % [pu] magnetising resistance from no-load loss Xm_pu = 1/sqrt((i0_pct/100)^2 - (1/Rm_pu)^2); % [pu] magnetising reactance from no-load current I_LV_rated = S_rated/(sqrt(3)*V_LV); % [A] rated secondary RMS line current %% 3. Thermal model constants (Source T1: Alliander transformer-thermal-model, % PowerTransformer ONAF defaults, an implementation of IEC 60076-7. % Replace with IEC 60076-7 / transformer test-report values when available.) dTheta_or = 60; % [K] top-oil temperature rise at rated load (T1: top_oil_temp_rise) g_r = 17; % [K] average winding-to-oil gradient (T1: winding_oil_gradient) H_hs = 1.3; % [-] hot-spot factor (T1: hot_spot_fac) tau_o_min = 150; % [min] oil time constant (T1: time_const_oil) tau_w_min = 7; % [min] winding time constant (T1: time_const_windings) k11 = 0.5; % [-] thermal model constant (T1: oil_const_k11) k21 = 2; % [-] thermal model constant (T1: winding_const_k21) k22 = 2; % [-] thermal model constant (T1: winding_const_k22) x_oil = 0.8; % [-] oil exponent (T1: oil_exp_x) y_wdg = 1.3; % [-] winding exponent (T1: winding_exp_y) %% 4. Derived thermal-network values (thermal-electrical analogy; guide Section A3) dTheta_hr = H_hs * g_r; % [K] rated hot-spot-to-top-oil gradient P_tot_r = P0 + Pk; % [W] total loss at rated load R_th_oil = dTheta_or / P_tot_r; % [K/W] oil-to-ambient thermal resistance C_th_oil = k11*tau_o_min*60 / R_th_oil; % [J/K] oil thermal capacitance (R*C = k11*tau_o) R_th_h = 1; % [K/W] analogue resistance for hot-spot networks (scaling, see A3) C_th_h1 = k22*tau_w_min*60 / R_th_h; % [J/K] (R*C = k22*tau_w) C_th_h2 = (tau_o_min/k22)*60 / R_th_h; % [J/K] (R*C = tau_o/k22) cp_unit = 1; % [J/(kg*K)] unit specific heat so that block "mass" = capacitance %% 5. Operating scenario theta_amb_C = 20; % [degC] ambient temperature (IEC reference ambient; replace with site data) K_load = 1.0; % [pu] constant load factor for the verification run P_load_min = 1e-3*S_rated; % [W] minimum load power required by the variable-load block (> 0) t_stop = 24*3600;% [s] simulation stop time t_step_max = 60; % [s] maximum solver step (well below the 7 min winding time constant) % Load profile as a timeseries: time [s], load factor [pu] load_profile = timeseries([K_load; K_load], [0; t_stop]); %% 6. Insulation ageing (relative ageing rate, normal Kraft paper) theta_ref_age = 98; % [degC] hot-spot temperature giving relative ageing rate = 1 dT_double_age = 6; % [K] temperature increase that doubles the ageing rate

## A3. How the derived values are obtained

### A3.1 Electrical equivalent circuit (per unit on the transformer rating)

- Load loss: Pk = (ukr/100)·S_rated = 136 kW, because the resistive short-circuit voltage in per unit equals the copper loss in per unit.

- Series resistance R = ukr/100 = 0.0034 pu; leakage reactance X = √(uk² − ukr²)/100 = 0.16196 pu.

- Assumption A1: R and X are split equally between the two windings. This is the usual assumption when only short-circuit test data are available. It does not change the terminal behaviour.

- Magnetising resistance Rm = S_rated/P0 = 2222.2 pu (the core loss in per unit is 1/Rm). Magnetising reactance from the no-load current: |1/Rm + 1/(jXm)| = i0, giving Xm = 1/√(i0² − (1/Rm)²) = 4588.3 pu. MathWorks uses the same relation in the documentation of the Two-Winding Transformer (Three-Phase) block.

- Rated secondary current I_LV_rated = S_rated/(√3·V_LV) = 1154.70 A.

### A3.2 Thermal model as a thermal circuit

The IEC 60076-7 loading guide gives the top-oil and hot-spot temperatures as differential equations for a time-varying load factor K. The form used here (as implemented in the Alliander open-source IEC 60076-7 model, T1) is:

k11·tau_o · d(dTheta_o)/dt = dTheta_or·[(1 + R·K²)/(1 + R)]^x − dTheta_o (top-oil rise) k22·tau_w · d(dTheta_h1)/dt = k21·dTheta_hr·K^y − dTheta_h1 (tau_o/k22)·d(dTheta_h2)/dt = (k21 − 1)·dTheta_hr·K^y − dTheta_h2 theta_hs = theta_amb + dTheta_o + dTheta_h1 − dTheta_h2, R = Pk/P0, dTheta_hr = H·g_r

Each equation has the form RC·dθ/dt = R·Q − θ. That is exactly the equation of a thermal mass C, heated by a heat flow Q and cooled through a thermal resistance R. Simscape solves it with real thermal blocks:

- Top-oil circuit: R_th_oil = dTheta_or/P_tot_r and C_th_oil = k11·tau_o/R_th_oil, so R·C = k11·tau_o. Heat input Q_oil = P_tot_r·[(P0 + Pk·K²)/P_tot_r]^x, so R·Q_oil equals the IEC ultimate top-oil rise. At rated load Q_oil equals the real total loss P0 + Pk = 154 kW.

- Hot-spot circuits: two analogue R-C circuits with R_th_h = 1 K/W, C_th_h1 = k22·tau_w and C_th_h2 = tau_o/k22. They are driven by Q_h1 = k21·dTheta_hr·K^y/R_th_h and Q_h2 = (k21−1)·dTheta_hr·K^y/R_th_h. Their node temperatures above ambient equal dTheta_h1 and dTheta_h2. The value 1 K/W is a scaling choice; only the product R·C is physical.

- Ageing: relative ageing rate for normal Kraft paper V = 2^((theta_hs − 98)/6): V = 1 at 98 °C and doubles every 6 K, as tabulated from IEC 60076-7 in the IntechOpen chapter (A4, ref T2).

## A4. Sources of the parameter values

| Code | Source | What it supplies | Status |
| --- | --- | --- | --- |
| E1 | pandapower, "Basic Standard Types", transformer type "40 MVA 110/20 kV" (pandapower documentation, readthedocs, accessed 3 Oct 2026). The page notes the types are for 50 Hz systems. | S_rated, V_HV, V_LV, uk, ukr, P0, i0 | Published typical data; replace with a real nameplate if a utility provides one |
| T1 | Alliander N.V., transformer-thermal-model (open source, MPL-2.0), class PowerTransformer, ONAF default specifications; an implementation of IEC 60076-7. | dTheta_or, g_r, H, tau_o, tau_w, k11, k21, k22, x, y | Default values; to be checked against IEC 60076-7:2018 when the standard is obtained |
| T2 | IntechOpen chapter "Thermal Modelling of Electrical Insulation System in Power Transformers", Table 1 (relative ageing rate, from IEC 60076-7). | theta_ref_age = 98 °C, doubling every 6 K | Secondary source; check against the standard |
| — | Scenario choices | theta_amb_C = 20 °C (verification), load_profile, t_stop | To be replaced by site ambient data and a cited load profile |

## A5. Room for the standards: what to replace when they arrive

- IEC 60076-7:2018: check the thermal equations of Section A3.2. Replace the T1 values with the table of recommended thermal characteristics for the cooling class, or with the heat-run test report of a real transformer. Only Section 3 of params_transformer.m changes.

- IEC 60599 / IEEE C57.104 / Duval (2002): transcribe the ratio limits and Duval zone vertices into 02_Standards/rogers_ratio_table.csv, iec_ratio_table.csv and duval_triangle_zones.csv, with column names exactly as in the comments of conventional_diagnosis.m. No code changes are needed: the diagnoses switch from PENDING_STANDARD to real classes automatically.

- A real transformer nameplate (for example from GRIDCo or ECG): replace Section 1 of params_transformer.m.

## A6. Supporting functions (provided and tested)

| File | Purpose | Inputs → outputs |
| --- | --- | --- |
| run_transformer_simulation.m | Runs the Simulink model and packages the results; computes equivalent ageing hours | optional load profile timeseries → struct t_h, K_pu, theta_oil_C, theta_hs_C, ageing_V, loss_of_life_h |
| load_dga_record.m | Reads one measured record from a CSV/XLSX file (the measured-DGA playback) | file, row → gas struct, table row |
| gas_ratios.m | Rogers/IEC/Doernenburg ratios and Duval Triangle percentages; zero denominators become NaN | gas struct → ratios struct |
| duval_xy.m | Converts Duval percentages to x-y coordinates of an equilateral triangle | %C2H4, %C2H2 → x, y |
| conventional_diagnosis.m | Applies limits read from the 02_Standards CSV files; returns PENDING_STANDARD until they exist, ND when no class applies | gas struct → rogers, iec, duval, ratios |
| plot_duval_triangle.m | Draws the triangle, zones (when available) and the sample point | axes, ratios, zone file → plot |
| ml_diagnose.m | Calls the FastAPI service; returns NOT_CONNECTED while ML_ENABLED = false | gas struct → status, fault_class, probabilities, latency |

Code of the two functions that link Simulink and the app to the outside world:

function res = run_transformer_simulation(load_profile_in) %RUN_TRANSFORMER_SIMULATION Simulate the transformer operating model. % res = run_transformer_simulation() uses load_profile from params_transformer.m % res = run_transformer_simulation(profile_ts) uses the given timeseries (time s, K pu) % Output struct res: t_h, K_pu, theta_oil_C, theta_hs_C, ageing_V, loss_of_life_h mdl = 'Transformer_Operating_Model'; load_system(mdl); in = Simulink.SimulationInput(mdl); if nargin == 1 in = in.setVariable('load_profile', load_profile_in); end out = sim(in); res.t_h = out.theta_oil_C.Time / 3600; res.K_pu = squeeze(out.K_pu.Data); res.theta_oil_C = squeeze(out.theta_oil_C.Data); res.theta_hs_C = squeeze(out.theta_hs_C.Data); res.ageing_V = squeeze(out.ageing_rate_V.Data); % Equivalent ageing in hours = integral of V over time (trapezoidal rule) res.loss_of_life_h = trapz(out.ageing_rate_V.Time, res.ageing_V) / 3600; end

function m = ml_diagnose(g) %ML_DIAGNOSE Ask the Python FastAPI service for the machine-learning diagnosis. % m = ml_diagnose(g), g = struct with H2, CH4, C2H6, C2H4, C2H2 (ppm). % Until the service exists (Phase 7), ML_ENABLED is false and the function % returns status "NOT_CONNECTED". To connect later, set ML_ENABLED = true % and check ML_URL; nothing else in the app has to change. ML_ENABLED = false; ML_URL = 'http://127.0.0.1:8000/diagnose'; m = struct('status', "NOT_CONNECTED", 'fault_class', "", 'probabilities', [], 'latency_s', NaN); if ~ML_ENABLED, return, end opts = weboptions('MediaType', 'application/json', 'Timeout', 10); tic; try resp = webwrite(ML_URL, g, opts); m.status = "OK"; m.fault_class = string(resp.fault_class); m.probabilities = resp.probabilities; catch ME m.status = "ERROR: " + string(ME.message); end m.latency_s = toc; end

Transition A → B When Part A is complete, params_transformer runs without error, and S_rated, C_th_oil, I_LV_rated and the other variables appear in the Workspace. The model in Part B reads these variables by name.

# PART B — Simulink and Simscape Transformer Model

## B1. Model layout

The model has seven subsystems. Four carry the electrical power path, a Simscape Electrical network. Three carry the thermal chain: a Simulink loss calculation, a Simscape thermal network, and outputs.

Figure B1. Top level of Transformer_Operating_Model (built and simulated in R2025b)

| Subsystem | Domain | Input(s) | Output(s) |
| --- | --- | --- | --- |
| SS1_Grid_Supply | Simscape Electrical | — | HV_out (three-phase) |
| SS2_Power_Transformer | Simscape Electrical | HV_in | LV_out (three-phase) |
| SS3_LV_Measurement | Simscape Electrical + Simulink | LV_in | LV_out (three-phase); K_pu (Simulink signal) |
| SS4_Variable_Load | Simscape Electrical + Simulink | LV_in | — (consumes power) |
| SS5_Losses_to_Heat | Simulink | K_pu | Q_oil, Q_h1, Q_h2 (W) |
| SS6_Thermal_Network | Simscape thermal (Foundation library) | Q_oil, Q_h1, Q_h2 | theta_oil_C (°C), dTheta_h1, dTheta_h2 (K) |
| SS7_Outputs_and_Ageing | Simulink | K_pu, theta_oil_C, dTheta_h1, dTheta_h2 | Logged: K_pu, theta_oil_C, theta_hs_C, ageing_rate_V |

Why the arithmetic is in Simulink blocks, not in physical-signal blocks The electrical network uses the Frequency and time equation formulation. This lets a 24-hour, 50 Hz simulation finish in about 10 seconds instead of hours. That formulation accepts only (switched-)linear equations. A nonlinear PS Math Function inside the network caused the error "Equations in frequency and time mode must be switched-linear" during verification. The square root, powers and products are therefore done with ordinary Simulink blocks, between converter blocks. The electrical and thermal parts are then two separate physical networks, and each has its own Solver Configuration block.

## B2. Create the model and set it up

- Run project_setup. In the MATLAB toolstrip choose Simulink > Blank Model. Save it immediately as Transformer_Operating_Model.slx in 05_Simulink_Model.

- Callbacks: Modeling tab > Model Settings (arrow) > Model Properties > Callbacks. In PreLoadFcn and in InitFcn type params_transformer;. Click OK. The parameters are now reloaded every time the model opens or runs.

- Solver: Modeling tab > Model Settings (Ctrl+E) > Solver. Set Stop time = t_stop, Type = Variable-step, Solver = ode23t, Max step size = t_step_max. Click OK.

- Model annotation: at the top of the canvas add: "TRANSFORMER OPERATING MODEL (operating context only - no gas values are generated). Electrical network: SS1 -> SS2 -> SS3 -> SS4. Thermal chain: SS3 (K) -> SS5 -> SS6 -> SS7. All parameters are defined in params_transformer.m (run by the InitFcn callback)."

## B3. Common procedures used in every subsystem

### B3.1 Making a subsystem

- From the Library Browser drag Simulink > Ports & Subsystems > Subsystem onto the canvas and rename it (for example SS1_Grid_Supply).

- Double-click to open it. Delete the default In1, Out1 and the line between them if the subsystem has no Simulink signals (SS1, SS2 and SS4 keep none; SS3 needs one Out1, SS5 to SS7 need In1/Out1 blocks as listed).

- Physical ports use Simscape > Utilities > Connection Port. Double-click it: set Port location on parent subsystem to Left or Right. Port number is shared by left and right ports, so number them 1, 2, 3… in the order given in each table. On each side the parent block shows them from top to bottom in increasing number.

### B3.2 Converter blocks

- Simulink-PS Converter (Simscape > Utilities): one Simulink input (left) and one physical-signal output (right). Set Input signal unit so Simscape knows the unit (for example W).

- PS-Simulink Converter (Simscape > Utilities): one physical-signal input (left) and one Simulink output (right). Set Output signal unit. For a temperature in °C also tick Apply affine conversion, so the 273.15 offset is applied.

- Every Simscape network needs exactly one Solver Configuration (Simscape > Utilities) connected anywhere on that network. Two on one network, or none, gives an error.

## B4. SS1_Grid_Supply — the 110 kV supply

Purpose: provides a stiff 110 kV, 50 Hz three-phase supply (an infinite bus: source impedance None).

| Block (name in model) | Library path | Ports (side) | Settings (variables only) | How it works |
| --- | --- | --- | --- | --- |
| Grid_Source | Simscape > Electrical > Sources > Voltage Source (Three-Phase) | 2: n (left), ~ (right, three-phase) | Rated voltage (phase-to-phase RMS) = V_HV [V]; Phase shift = phase_shift_deg [deg]; Frequency = f_rated [Hz]; Source impedance = None | Ideal source that keeps a balanced sinusoidal voltage at its terminals whatever current flows; n is the star point. |
| Ground | Simscape > Electrical > Connectors & References > Electrical Reference | 1 (top) | — | The zero-volt reference node of the electrical network. |
| Solver_Configuration | Simscape > Utilities > Solver Configuration | 1 (right) | Equation formulation = Frequency and time (other settings default) | Holds the solver settings for this physical network; Frequency and time lets 50 Hz networks run with large steps. |
| HV_out | Simscape > Utilities > Connection Port | 1 | Port location = Right; Port number = 1 | Carries the three-phase connection out of the subsystem. |

| # | From (block : port) | To (block : port) | What travels on the line |
| --- | --- | --- | --- |
| 1 | Grid_Source : n | Ground | Star point to earth |
| 2 | Solver_Configuration | Ground (same node) | Solver attached to the network |
| 3 | Grid_Source : ~ | HV_out | 110 kV three-phase |

Annotation: "SS1 GRID SUPPLY. Ideal three-phase source (infinite bus) at V_HV, f_rated. Output: HV_out (three-phase, composite). Parameters: V_HV, f_rated, phase_shift_deg. Solver Configuration sets the equation formulation for the electrical network."

## B5. SS2_Power_Transformer — the 40 MVA transformer

Purpose: the power transformer being monitored. Transition in: HV_in from SS1. Transition out: LV_out to SS3.

| Block (name in model) | Library path | Ports (side) | Settings (variables only) | How it works |
| --- | --- | --- | --- | --- |
| HV_in | Simscape > Utilities > Connection Port | 1 | Left; Port number 1 | Three-phase input from SS1. |
| Two_Winding_Transformer | Simscape > Electrical > Passive > Transformers > Two-Winding Transformer (Three-Phase) | 2: ~1 (left, primary), ~2 (right, secondary) | Rated apparent power = S_rated [V*A]; Rated electrical frequency = f_rated [Hz]; Winding 1 connection = Delta 1 o'clock; Primary rated voltage = V_HV [V]; Winding 2 connection = Wye with grounded neutral; Secondary rated voltage = V_LV [V]; Core type = Three-phase three-limb; Primary/Secondary winding resistance (pu) = Rw1_pu / Rw2_pu; Leakage reactance = Include; Primary/Secondary leakage reactance (pu) = Xl1_pu / Xl2_pu; Magnetizing resistance = Include; Shunt magnetizing resistance (pu) = Rm_pu; Magnetizing reactance = Include; Shunt magnetizing reactance (pu) = Xm_pu; Magnetic saturation = None | Linear non-ideal three-phase transformer: winding resistance and leakage reactance in series, core loss and magnetising current in a shunt branch, all in per unit of its rating. |
| LV_out | Simscape > Utilities > Connection Port | 1 | Right; Port number 2 | Three-phase 20 kV output. |

| # | From (block : port) | To (block : port) | What travels on the line |
| --- | --- | --- | --- |
| 1 | HV_in | Two_Winding_Transformer : ~1 | 110 kV three-phase |
| 2 | Two_Winding_Transformer : ~2 | LV_out | 20 kV three-phase |

Note on vector group: pandapower lists this type with a 150° phase shift. The block offers only Delta 1 o'clock or Delta 11 o'clock, so Delta 1 o'clock / grounded Wye is used. Phase displacement does not affect current magnitudes, losses or temperatures. State this in the thesis.

Annotation: "SS2 POWER TRANSFORMER. Two-winding three-phase transformer, Delta (HV), grounded Wye (LV). Input: HV_in. Output: LV_out. Parameters: S_rated, V_HV, V_LV, Rw1_pu, Rw2_pu, Xl1_pu, Xl2_pu, Rm_pu, Xm_pu."

## B6. SS3_LV_Measurement — current and load factor

Purpose: measures the three secondary currents and computes the load factor K, the RMS current divided by the rated current. For a balanced three-phase set, ia² + ib² + ic² is constant and equals 3·I_rms², so K = √((ia²+ib²+ic²)/3)/I_LV_rated is exact at every instant without filtering.

| Block (name in model) | Library path | Ports (side) | Settings (variables only) | How it works |
| --- | --- | --- | --- | --- |
| LV_in | Simscape > Utilities > Connection Port | 1 | Left; Port number 1 | Three-phase input from SS2. |
| LV_out | Simscape > Utilities > Connection Port | 1 | Right; Port number 2 | Three-phase output to SS4. |
| Current_Sensor_3ph | Simscape > Electrical > Sensors & Transducers > Current Sensor (Three-Phase) | 3: ~1 (left), I (right, upper, physical signal), ~2 (right, lower) | — | Ideal series ammeter for each phase; outputs the three currents as one 3-element physical signal. |
| PS_to_Simulink_I | Simscape > Utilities > PS-Simulink Converter | 2: PS in (left), out (right) | Output signal unit = A | Turns the measured current vector into a Simulink signal in amperes. |
| Sum_of_Squares | Simulink > Math Operations > Dot Product | 3: two inputs (left), output (right) | — | Dot product of the current vector with itself = ia² + ib² + ic². |
| Divide_by_3 | Simulink > Math Operations > Gain | in, out | Gain = 1/3 | Mean square value. |
| Square_Root | Simulink > Math Operations > Math Function | in, out | Function = sqrt | RMS current. |
| Per_Unit | Simulink > Math Operations > Gain | in, out | Gain = 1/I_LV_rated | Converts amperes to per unit of rated current. |
| K_pu | Simulink > Ports & Subsystems > Out1 | in | Port number 1 | Load-factor output of the subsystem. |

| # | From (block : port) | To (block : port) | What travels on the line |
| --- | --- | --- | --- |
| 1 | LV_in | Current_Sensor_3ph : ~1 | Three-phase power in |
| 2 | Current_Sensor_3ph : ~2 | LV_out | Three-phase power out |
| 3 | Current_Sensor_3ph : I | PS_to_Simulink_I : input | Currents (A, physical) |
| 4 | PS_to_Simulink_I : output | Sum_of_Squares : input 1 and input 2 (branch the line) | Currents (A) |
| 5 | Sum_of_Squares | Divide_by_3 → Square_Root → Per_Unit → K_pu | A², A², A, pu |

Annotation: "SS3 LV MEASUREMENT. Current Sensor (Three-Phase) measures ia, ib, ic on the LV side. K = sqrt((ia^2+ib^2+ic^2)/3)/I_LV_rated (exact RMS for a balanced set). Input: LV_in. Outputs: LV_out (pass-through), K_pu (Simulink signal, per unit). Parameter: I_LV_rated."

## B7. SS4_Variable_Load — the customer load

Purpose: a resistive three-phase load whose real power follows the load profile P = K(t)·S_rated. Unity power factor is an assumption to state in the thesis.

| Block (name in model) | Library path | Ports (side) | Settings (variables only) | How it works |
| --- | --- | --- | --- | --- |
| LV_in | Simscape > Utilities > Connection Port | 1 | Left; Port number 1 | Three-phase input from SS3. |
| Load_Profile | Simulink > Sources > From Workspace | out | Data = load_profile; Form output after final data value by = Holding final value | Plays the load-factor time series defined in the parameter file. |
| K_to_Power | Simulink > Math Operations > Gain | in, out | Gain = S_rated | Load factor to watts. |
| Min_Power | Simulink > Discontinuities > Saturation | in, out | Upper limit = inf; Lower limit = P_load_min | Keeps the power above the block's required minimum (> 0). |
| Power_to_PS | Simscape > Utilities > Simulink-PS Converter | in (left), PS out (right) | Input signal unit = W | Turns the power demand into a physical signal in watts. |
| Wye_Variable_Load | Simscape > Electrical > Passive > RLC Assemblies > Wye-Connected Variable Load | 3: P (left, upper, physical signal), ~ (left, lower, three-phase), n (right, neutral) | Rated voltage = V_LV [V]; Minimum real power = P_load_min [W] | Star-connected resistors whose value R = V_rated²/P is set continuously from the power demand P. |
| Ground | Simscape > Electrical > Connectors & References > Electrical Reference | 1 | — | Earths the load star point. |

| # | From (block : port) | To (block : port) | What travels on the line |
| --- | --- | --- | --- |
| 1 | LV_in | Wye_Variable_Load : ~ | 20 kV three-phase |
| 2 | Wye_Variable_Load : n | Ground | Neutral to earth |
| 3 | Load_Profile → K_to_Power → Min_Power → Power_to_PS | Wye_Variable_Load : P | pu → W → W (physical) |

Annotation: "SS4 VARIABLE LOAD. Resistive three-phase load whose real power follows the load profile: P = K(t)*S_rated (unity power factor, assumption). Input: LV_in. Parameters: load_profile, S_rated, V_LV, P_load_min."

## B8. SS5_Losses_to_Heat — from load factor to heat inputs

Purpose: computes the three heat inputs of the thermal circuits from K (Section A3.2). Transition in: K_pu from SS3. Transition out: Q_oil, Q_h1, Q_h2 in watts to SS6.

| Block (name in model) | Library path | Ports (side) | Settings (variables only) | How it works |
| --- | --- | --- | --- | --- |
| K_pu | Simulink > Ports & Subsystems > In1 | out | Port number 1 | Load factor from SS3. |
| K_squared | Simulink > Math Operations > Math Function | in, out | Function = square | K². |
| Load_Loss_Pk | Simulink > Math Operations > Gain | in, out | Gain = Pk | Copper loss Pk·K² (W). |
| Plus_No_Load_Loss_P0 | Simulink > Math Operations > Bias | in, out | Bias = P0 | Total loss P0 + Pk·K² (W). |
| Normalise | Simulink > Math Operations > Gain | in, out | Gain = 1/P_tot_r | Total loss as a fraction of rated total loss. |
| Exponent_x | Simulink > Sources > Constant | out | Constant value = x_oil | Oil exponent. |
| Power_x | Simulink > Math Operations > Math Function | 2 in (u = base, v = exponent), out | Function = pow | Raises the loss ratio to the power x. |
| Q_oil_Gain | Simulink > Math Operations > Gain | in, out | Gain = P_tot_r | Equivalent oil heat input Q_oil (W). |
| Exponent_y | Simulink > Sources > Constant | out | Constant value = y_wdg | Winding exponent. |
| K_power_y | Simulink > Math Operations > Math Function | 2 in, out | Function = pow | K^y. |
| Q_h1_Gain | Simulink > Math Operations > Gain | in, out | Gain = k21*dTheta_hr/R_th_h | Heat drive of hot-spot circuit 1 (W). |
| Q_h2_Gain | Simulink > Math Operations > Gain | in, out | Gain = (k21-1)*dTheta_hr/R_th_h | Heat drive of hot-spot circuit 2 (W). |
| Q_oil, Q_h1, Q_h2 | Simulink > Ports & Subsystems > Out1 | in | Port numbers 1, 2, 3 | Outputs to SS6. |

| # | From (block : port) | To (block : port) | What travels on the line |
| --- | --- | --- | --- |
| 1 | K_pu | K_squared → Load_Loss_Pk → Plus_No_Load_Loss_P0 → Normalise | pu → W → W → pu |
| 2 | Normalise ; Exponent_x | Power_x : u ; Power_x : v | base and exponent |
| 3 | Power_x → Q_oil_Gain | Q_oil (Out 1) | W |
| 4 | K_pu ; Exponent_y | K_power_y : u ; K_power_y : v | base and exponent |
| 5 | K_power_y | Q_h1_Gain → Q_h1 (Out 2) and Q_h2_Gain → Q_h2 (Out 3) | W |

Annotation: "SS5 LOSSES TO HEAT. Total loss P0 + Pk*K^2; equivalent oil heat input Q_oil = P_tot_r*((P0+Pk*K^2)/P_tot_r)^x; hot-spot drives Q_h1 = k21*dTheta_hr*K^y/R_th_h and Q_h2 = (k21-1)*dTheta_hr*K^y/R_th_h (IEC 60076-7 differential-equation model). Outputs in W."

## B9. SS6_Thermal_Network — oil and hot-spot thermal circuits

Purpose: three thermal R-C circuits built from Simscape Foundation thermal blocks (Simscape > Foundation Library > Thermal). The oil circuit is the physical oil and tank heat capacity cooled to ambient. The two hot-spot circuits produce the hot-spot rise components. Build the oil circuit first, then repeat the same pattern for HS1 and HS2.

| Block (name in model) | Library path | Ports (side) | Settings (variables only) | How it works |
| --- | --- | --- | --- | --- |
| Q_oil, Q_h1, Q_h2 | Simulink > Ports & Subsystems > In1 | out | Port numbers 1, 2, 3 | Heat inputs from SS5. |
| Heat_to_PS_Oil / _HS1 / _HS2 | Simscape > Utilities > Simulink-PS Converter | in, PS out | Input signal unit = W | Heat flow command as a physical signal. |
| Heat_Source_Oil / _HS1 / _HS2 | Simscape > Foundation Library > Thermal > Thermal Sources > Controlled Heat Flow Rate Source | 3: B (top, outlet), S (bottom, physical signal), A (bottom, inlet) | — | Ideal source pushing the commanded heat flow from A to B, whatever the temperatures. |
| Thermal_Reference | Simscape > Foundation Library > Thermal > Thermal Elements > Thermal Reference | 1 (top) | — | Absolute-zero reference; the A ports of all three sources connect here. One block shared by all three circuits. |
| Thermal_Mass_Oil / _HS1 / _HS2 | Simscape > Foundation Library > Thermal > Thermal Elements > Thermal Mass | 1 (top) | Mass = C_th_oil / C_th_h1 / C_th_h2 [kg]; Specific heat = cp_unit [J/(kg*K)]; Initial Targets > Temperature: Priority High, Value = theta_amb_C + 273.15 [K] | Stores heat: temperature rises at the rate (heat in − heat out)/(mass × specific heat). With cp_unit = 1, mass equals the heat capacity in J/K. |
| Thermal_Resistance_Oil / _HS1 / _HS2 | Simscape > Foundation Library > Thermal > Thermal Elements > Thermal Resistance | 2: A (left), B (right) | Thermal resistance = R_th_oil / R_th_h / R_th_h [K/W] | Heat flow = temperature difference / resistance; models cooling to ambient. |
| Ambient_Temperature | Simscape > Foundation Library > Thermal > Thermal Sources > Temperature Source | 1 (top) | Temperature = theta_amb_C + 273.15 [K] | Holds the surroundings at ambient temperature. One block shared by all three circuits. |
| Temperature_Sensor_Oil | Simscape > Foundation Library > Thermal > Thermal Sensors > Temperature Sensor | 2: A (left), T (right) | Temperature measurement = Absolute | Outputs the absolute temperature of node A. |
| Temperature_Sensor_HS1 / _HS2 | same as above | 3: A (left), B (right, upper), T (right, lower) | Temperature measurement = Difference | Outputs T(A) − T(B): the rise of the node above ambient. |
| PS_to_Simulink_Oil | Simscape > Utilities > PS-Simulink Converter | PS in, out | Output signal unit = degC; Apply affine conversion = ticked | Top-oil temperature in °C. |
| PS_to_Simulink_HS1 / _HS2 | Simscape > Utilities > PS-Simulink Converter | PS in, out | Output signal unit = K | Hot-spot rise components in kelvin. |
| theta_oil_C, dTheta_h1, dTheta_h2 | Simulink > Ports & Subsystems > Out1 | in | Port numbers 1, 2, 3 | Outputs to SS7. |
| Solver_Configuration_Thermal | Simscape > Utilities > Solver Configuration | 1 | Defaults (Equation formulation = Time) | Solver for the thermal network (a separate physical network from the electrical one). |

Connections for one circuit (repeat for Oil, HS1, HS2):

| # | From (block : port) | To (block : port) | What travels on the line |
| --- | --- | --- | --- |
| 1 | Q_x (In) | Heat_to_PS_x : input | Heat command (W) |
| 2 | Heat_to_PS_x : output | Heat_Source_x : S | Heat command (physical, W) |
| 3 | Heat_Source_x : A | Thermal_Reference | Heat drawn from the reference |
| 4 | Heat_Source_x : B | Thermal_Mass_x | Heat delivered to the node |
| 5 | Thermal_Mass_x | Thermal_Resistance_x : A | Node to cooling path |
| 6 | Thermal_Resistance_x : B | Ambient_Temperature | Cooling to ambient |
| 7 | Thermal_Mass_x | Temperature_Sensor_x : A | Node temperature |
| 8 | Temperature_Sensor_HSx : B (HS1, HS2 only) | Ambient_Temperature | Reference for the difference |
| 9 | Temperature_Sensor_x : T | PS_to_Simulink_x → Out (theta_oil_C / dTheta_h1 / dTheta_h2) | °C or K |
| 10 | Solver_Configuration_Thermal | Thermal_Reference | Solver attached to the thermal network |
| Two errors found during verification, and the fixes already built in "Temperature must be greater than absolute zero": the hot-spot circuits were first referenced to 0 K. They are now cooled to the ambient source and start at ambient. Their sensors measure the difference to ambient. "Each physical network must be connected to exactly one Solver Configuration": the three circuits are joined into one network through the shared Thermal_Reference and Ambient_Temperature blocks, which carry the single Solver_Configuration_Thermal. |  |  |  |

Annotation: "SS6 THERMAL NETWORK. Three first-order thermal R-C circuits. Oil: C_th_oil, R_th_oil to ambient; top-oil time constant R*C = k11*tau_o. HS1, HS2: analogue circuits whose node temperatures equal the hot-spot rise components dTheta_h1, dTheta_h2 above ambient (R*C = k22*tau_w and tau_o/k22). This is a separate physical network and needs its own Solver Configuration."

## B10. SS7_Outputs_and_Ageing — results to the workspace

| Block (name in model) | Library path | Ports (side) | Settings (variables only) | How it works |
| --- | --- | --- | --- | --- |
| K_pu, theta_oil_C, dTheta_h1, dTheta_h2 | Simulink > Ports & Subsystems > In1 | out | Port numbers 1–4 | Inputs from SS3 and SS6. |
| Hot_Spot_Sum | Simulink > Math Operations > Sum | 3 in, out | List of signs = ++- | theta_hs = theta_oil + dTheta_h1 − dTheta_h2. |
| Minus_Reference | Simulink > Math Operations > Bias | in, out | Bias = -theta_ref_age | theta_hs − 98. |
| Ageing_Gain | Simulink > Math Operations > Gain | in, out | Gain = log(2)/dT_double_age | Scales so that every 6 K doubles the rate. |
| Exp | Simulink > Math Operations > Math Function | in, out | Function = exp | Relative ageing rate V. |
| Log_K_pu, Log_theta_oil_C, Log_theta_hs_C, Log_ageing_rate_V | Simulink > Sinks > To Workspace | in | Variable name = K_pu / theta_oil_C / theta_hs_C / ageing_rate_V; Save format = Timeseries | Stores each signal in the simulation output for MATLAB and the app. |

| # | From (block : port) | To (block : port) | What travels on the line |
| --- | --- | --- | --- |
| 1 | theta_oil_C ; dTheta_h1 ; dTheta_h2 | Hot_Spot_Sum : 1 ; 2 ; 3 | °C, K, K |
| 2 | Hot_Spot_Sum | Minus_Reference → Ageing_Gain → Exp | °C → K → – → V |
| 3 | K_pu ; theta_oil_C ; Hot_Spot_Sum ; Exp | Log_K_pu ; Log_theta_oil_C ; Log_theta_hs_C ; Log_ageing_rate_V | logged signals |

Annotation: "SS7 OUTPUTS AND AGEING. Hot-spot temperature theta_hs = theta_oil + dTheta_h1 - dTheta_h2; relative ageing rate V = 2^((theta_hs - theta_ref_age)/dT_double_age). Logged to the workspace: K_pu, theta_oil_C, theta_hs_C, ageing_rate_V." Optionally add a Scope on theta_oil_C and Hot_Spot_Sum for viewing.

## B11. Top-level connections

| # | From (block : port) | To (block : port) | What travels on the line |
| --- | --- | --- | --- |
| 1 | SS1_Grid_Supply : HV_out | SS2_Power_Transformer : HV_in | 110 kV three-phase |
| 2 | SS2_Power_Transformer : LV_out | SS3_LV_Measurement : LV_in | 20 kV three-phase |
| 3 | SS3_LV_Measurement : LV_out | SS4_Variable_Load : LV_in | 20 kV three-phase |
| 4 | SS3_LV_Measurement : K_pu | SS5_Losses_to_Heat : K_pu and SS7 : K_pu (branch) | load factor (pu) |
| 5 | SS5 : Q_oil, Q_h1, Q_h2 | SS6 : Q_oil, Q_h1, Q_h2 | heat inputs (W) |
| 6 | SS6 : theta_oil_C, dTheta_h1, dTheta_h2 | SS7 : inputs 2, 3, 4 | °C, K, K |

## B12. Run and verify

- Press Ctrl+D (Update Diagram). Fix any error before simulating; Section B13 lists the ones met during verification.

- Click Run. A 24-hour simulation takes about 10 seconds on the project computer.

- In the Command Window: res = run_transformer_simulation(); plot(res.t_h, res.theta_oil_C, res.t_h, res.theta_hs_C).

- Compare with the expected results below. If your values differ by more than 0.1 K, compare your blocks with the model built by reference_build/build_transformer_model.m.

| Check (verification run, ambient 20 °C) | Expected (from IEC equations) | Simscape model result |
| --- | --- | --- |
| Load factor at rated power demand (resistive load at rated voltage, after the 16.2 % impedance drop) | — | K = 0.9839 |
| Test 1: final top-oil temperature, 24 h at rated demand | 78.638 °C | 78.638 °C |
| Test 1: final hot-spot temperature | 100.276 °C | 100.276 °C |
| Test 1: time to 63 % of top-oil rise | k11·tau_o = 75.0 min | 75.0 min |
| Test 1: largest difference model − equations after 10 min | 0 | 0.006 K (oil), 0.061 K (hot-spot) |
| Test 2: load step 0.6 → 1.2 pu at 6 h, largest difference | 0 | 0.003 K (oil), 0.031 K (hot-spot) |
| Test 2: final top-oil and hot-spot | — | 95.50 °C and 122.70 °C |

Figure B2. Simscape model (solid) against an independent ode45 solution of the IEC 60076-7 equations (dotted)

## B13. Errors met during verification and how to fix them

| Message (shortened) | Cause | Fix |
| --- | --- | --- |
| Equations in frequency and time mode must be switched-linear | Nonlinear physical-signal block (PS Math Function) inside the electrical network | Do the arithmetic with Simulink blocks after a PS-Simulink Converter (as in SS3) |
| Multiple Solver Configuration blocks connected to Physical Network | Two solvers on one network (networks joined by physical-signal lines count as one) | Keep exactly one per network |
| There is no Solver Configuration block connected to Physical Network | A thermal circuit not joined to the others | Use the shared Thermal_Reference and Ambient_Temperature blocks |
| Temperature must be greater than absolute zero | Thermal mass started at 0 K | Initial temperature = theta_amb_C + 273.15 K |
| Ports appear on the wrong side or in the wrong order | Connection Port numbers repeated on left and right | Port numbers are unique across both sides |
| Simulation runs but results are empty | Drive C: full; MATLAB disabled recording | Free space on C: |

Transition B → C Part B is complete when res = run_transformer_simulation() returns the values in Section B12. The app calls exactly this function, so the dashboard shows the verified model output.

# PART C — MATLAB App (App Designer Dashboard)

The app is the engineer's screen. It does four things. It runs the transformer simulation and plots the operating temperatures. It loads a measured DGA file and selects a record. It diagnoses the record with the conventional methods and the ML service, and plots it on the Duval Triangle. It shows whether the methods agree. A version written in code, DGADashboard_reference.m, was created and exercised in R2025b with the same components and callbacks; Figure C1 shows it.

Figure C1. Reference dashboard after a simulation run and a diagnosis. Conventional thresholds and the ML service are not yet connected, so they show PENDING_STANDARD and NOT_CONNECTED. The gas values are a software test input, not data.

## C1. Create the app

- Run project_setup. Type appdesigner and choose Blank App.

- Save it immediately as DGADashboard.mlapp in 10_Dashboard_Client.

- In Design View, from the Component Library, drag a Grid Layout onto the figure. In the Inspector set ColumnWidth = 260, 1x, 1x and RowHeight = 1x, 1x, 60.

## C2. Components

Add the components below. Rename each in the Component Browser (double-click the name) exactly as listed, because the callback code uses these names. Set the grid row and column in the Inspector under Layout.

| Component (Library) | Name | Grid position / parent | Properties to set |
| --- | --- | --- | --- |
| Panel | ControlPanel | Row 1–3, Column 1 | Title = Controls; inside it add a Grid Layout with 7 rows: 40, 40, 22, 30, 40, 1x, 60 |
| Button | RunSimulationButton | ControlPanel row 1 | Text = Run transformer simulation |
| Button | LoadDGAFileButton | ControlPanel row 2 | Text = Load measured DGA file |
| Label | RecordSpinnerLabel | ControlPanel row 3 | Text = Record number (row) |
| Spinner | RecordSpinner | ControlPanel row 4 | Limits = 1 1; Value = 1; RoundFractionalValues = on |
| Button | DiagnoseButton | ControlPanel row 5 | Text = Diagnose selected record |
| Table | GasTable | ControlPanel row 6 | ColumnName = Gas, ppm |
| Label | StatusLabel | ControlPanel row 7 | WordWrap = on |
| Axes | UIAxesTemperature | Row 1, Columns 2–3 | Title = Transformer operating condition (simulated) |
| Axes | UIAxesDuval | Row 2, Column 2 | Title = Duval Triangle 1 (measured sample) |
| Table | ResultsTable | Row 2, Column 3 | ColumnName = Method, Diagnosis |
| Lamp | AgreementLamp | Row 3, Columns 2–3 (in a 1×2 Grid Layout, ColumnWidth 40, 1x) | Color = grey |
| Label | AgreementLabel | next to the lamp | Text = Agreement: not available; FontWeight = bold |

## C3. Properties

In Code View, click Property > Private Property and replace the template with:

properties (Access = private) SimResult % struct returned by run_transformer_simulation DGAFile % full path of the measured DGA file Gas % struct with H2, CH4, C2H6, C2H4, C2H2 of the current record Info % table row of the current record (traceability) end

## C4. Callbacks

Add each callback, then paste the body. Startup: in the Component Browser select the top node (the app), go to Callbacks > StartupFcn and choose add. Buttons: right-click the button > Callbacks > Add ButtonPushedFcn callback. App Designer writes the first and last lines; paste only the lines between them.

### C4.1 startupFcn

evalin('base', 'params_transformer;'); app.StatusLabel.Text = 'Ready. Run the simulation or load a DGA file.'; app.AgreementLamp.Color = [0.6 0.6 0.6];

### C4.2 RunSimulationButtonPushed

app.StatusLabel.Text = 'Simulating transformer operation...'; drawnow; app.SimResult = run_transformer_simulation(); r = app.SimResult; plot(app.UIAxesTemperature, r.t_h, r.theta_oil_C, 'b', r.t_h, r.theta_hs_C, 'r', 'LineWidth', 1.3); xlabel(app.UIAxesTemperature, 'Time (h)'); ylabel(app.UIAxesTemperature, 'Temperature (\circC)'); legend(app.UIAxesTemperature, 'Top-oil', 'Hot-spot', 'Location', 'southeast'); grid(app.UIAxesTemperature, 'on'); app.StatusLabel.Text = sprintf('Simulation done. Final hot-spot %.1f °C, ageing %.1f h.', ... r.theta_hs_C(end), r.loss_of_life_h);

### C4.3 LoadDGAFileButtonPushed

[f, p] = uigetfile({'*.csv;*.xlsx', 'DGA files'}, 'Select measured DGA file'); if isequal(f, 0), return, end app.DGAFile = fullfile(p, f); n = height(readtable(app.DGAFile)); app.RecordSpinner.Limits = [1 n]; app.RecordSpinner.Value = 1; app.StatusLabel.Text = sprintf('Loaded %s (%d records).', f, n);

### C4.4 DiagnoseButtonPushed

if isempty(app.DGAFile) app.StatusLabel.Text = 'Load a DGA file first.'; return end [app.Gas, app.Info] = load_dga_record(app.DGAFile, app.RecordSpinner.Value); g = app.Gas; d = conventional_diagnosis(g); m = ml_diagnose(g); app.GasTable.Data = table(["H2"; "CH4"; "C2H6"; "C2H4"; "C2H2"], ... [g.H2; g.CH4; g.C2H6; g.C2H4; g.C2H2], 'VariableNames', {'Gas', 'ppm'}); app.ResultsTable.Data = table(["Rogers Ratio"; "IEC 60599 ratio"; "Duval Triangle 1"; "Machine learning"], ... [string(d.rogers); string(d.iec); string(d.duval); m.status + " " + m.fault_class], ... 'VariableNames', {'Method', 'Diagnosis'}); root = fileparts(fileparts(which('conventional_diagnosis'))); plot_duval_triangle(app.UIAxesDuval, d.ratios, fullfile(root, '02_Standards', 'duval_triangle_zones.csv')); app.updateAgreement(d, m);

### C4.5 Helper function updateAgreement

In Code View click Function > Private Function, name it updateAgreement(app, d, m), and paste:

conv = [string(d.rogers), string(d.iec), string(d.duval)]; if m.status ~= "OK" ¦¦ any(conv == "PENDING_STANDARD") app.AgreementLamp.Color = [0.6 0.6 0.6]; % grey: not yet comparable app.AgreementLabel.Text = 'Agreement: not available'; elseif all(conv == m.fault_class) app.AgreementLamp.Color = [0 0.7 0]; % green: all agree app.AgreementLabel.Text = 'Agreement: all methods agree'; else app.AgreementLamp.Color = [0.9 0.5 0]; % amber: disagreement app.AgreementLabel.Text = 'Agreement: methods disagree'; end

## C5. Test the app

- Click Run in App Designer. Press Run transformer simulation: the temperature plot of Figure C1 appears and the status shows a final hot-spot of about 100.3 °C.

- Press Load measured DGA file and choose a processed file from 03_Data/processed (once Phase 1 is complete). Choose a row and press Diagnose selected record.

- Until the standards are transcribed and the ML service exists, the results table shows PENDING_STANDARD and NOT_CONNECTED, and the lamp stays grey. This is intended: the app never shows a diagnosis that has not been implemented.

- Compare your app with DGADashboard_reference (type its name in the Command Window).

## C6. Connecting the machine-learning service later (Phase 7)

- Start the FastAPI service from 09_API_FastAPI.

- In ml_diagnose.m set ML_ENABLED = true and check ML_URL.

- The service must accept JSON {"H2":…, "CH4":…, "C2H6":…, "C2H4":…, "C2H2":…} and return {"fault_class": "…", "probabilities": […]}. These field names are fixed now so that Python and MATLAB match.

- Nothing in the app changes. The ML row and the agreement lamp become active automatically.

What the app must never do Show a diagnosis from a method whose thresholds have not been transcribed and checked; generate or alter gas values; or present the simulated operating condition as if it caused the measured gases. The simulation is context only.

# PART D — Final Checklist and References

## D1. Checklist before the work is accepted

- params_transformer.m runs; every variable has a unit and a source code.

- No block dialog contains a parameter number: open each block and check that every field holds a variable name (or a mathematical constant).

- Every subsystem and the top level has its annotation.

- Update Diagram gives no errors; a 24 h run reproduces the values of Section B12 within 0.1 K.

- run_transformer_simulation returns non-empty results.

- The app runs, plots and shows PENDING_STANDARD / NOT_CONNECTED until those parts exist.

- A second team member has checked the build against the reference script.

## D2. References used in this guide

- MathWorks, Simscape Electrical documentation: Two-Winding Transformer (Three-Phase); Voltage Source (Three-Phase); Wye-Connected Variable Load; Current Sensor (Three-Phase). https://www.mathworks.com/help/sps/ (accessed 3 Oct 2026). The online pages describe R2026b; ports and parameters were confirmed in the installed R2025b libraries.

- MathWorks, Simscape documentation: Controlled Heat Flow Rate Source. https://www.mathworks.com/help/simscape/ref/controlledheatflowratesource.html (accessed 3 Oct 2026).

- MATLAB Answers, "How to build now that Specialized Power Systems library is GONE" and related threads on R2025b (accessed 3 Oct 2026). https://www.mathworks.com/matlabcentral/answers/2181553

- pandapower, "Basic Standard Types" (transformer type 40 MVA 110/20 kV). https://pandapower.readthedocs.io/en/latest/std_types/basic.html (accessed 3 Oct 2026).

- Alliander N.V., transformer-thermal-model (IEC 60076-7 implementation, MPL-2.0), file transformer_thermal_model/transformer/power.py. https://github.com/alliander-opensource/transformer-thermal-model (accessed 3 Oct 2026).

- IntechOpen, "Thermal Modelling of Electrical Insulation System in Power Transformers", Table 1. https://www.intechopen.com/chapters/61792 (accessed 3 Oct 2026). Author details to be added from the publisher page.

- IEC 60076-7:2018, Power transformers – Part 7: Loading guide for mineral-oil-immersed power transformers. To be obtained; the values marked T1 will be checked against it.