PROJECT OVERVIEW AND OBJECTIVES

Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning: An Integrated MATLAB/Simulink–Python Framework

Justice — BSc Electrical and Electronic Engineering, University of Mines and Technology (UMaT), Tarkwa

# 1. Background and Need

Power transformers are among the most critical and capital-intensive assets in electrical transmission and distribution networks. Undetected incipient faults — partial discharge, low- and high-energy discharge, thermal faults, and arcing — can escalate into catastrophic failures, producing costly unplanned outages, safety hazards, and expensive replacement or repair.

Dissolved Gas Analysis (DGA) is the internationally recognized diagnostic technique (IEC 60599, IEEE C57.104) for detecting such faults from gases dissolved in transformer insulating oil. However, conventional interpretation methods — the Rogers Ratio, IEC Ratio, Duval Triangle, and Doernenburg Ratio — rely on fixed threshold and ratio rules derived from limited historical datasets. These methods frequently produce inconclusive or borderline classifications and can disagree with one another on the same sample.

A further, practically important gap exists: many field-deployable online DGA monitors measure only a reduced subset of gases (commonly omitting C₂H₆ and/or CO₂) due to sensor cost and technology constraints, yet conventional interpretation standards were designed assuming the full gas panel. Whether data-driven diagnosis can close this gap is largely underexplored in the literature.

# 2. Problem Statement / Research Gap

Can machine learning models trained on full dissolved-gas panels retain acceptable diagnostic accuracy when restricted to reduced, field-realistic gas subsets — and how does that accuracy compare with conventional DGA interpretation standards evaluated on the same data?

# 3. Aim

To develop, validate, and benchmark a machine-learning-based diagnostic framework for power transformer incipient-fault classification using Dissolved Gas Analysis — explicitly evaluating performance under both full and reduced gas-subset conditions — and to demonstrate the framework's practical applicability through an integrated MATLAB/Simulink–Python engineering architecture.

# 4. Specific Objectives

- Review and critically evaluate conventional DGA interpretation standards (IEC 60599, Rogers Ratio, Doernenburg Ratio, Duval Triangle) to establish quantitative accuracy and limitation benchmarks.

- Source and preprocess a validated DGA dataset with independently confirmed fault labels, applying missing-value handling, outlier treatment, feature scaling, and class-balancing — with scaling fitted only on training data to prevent leakage.

- Engineer diagnostic features from raw gas concentrations, including established diagnostic gas ratios, and select features using statistically justified techniques.

- Design, train, and evaluate multiple supervised classifiers (SVM, Random Forest, XGBoost, ANN) using stratified k-fold cross-validation, reporting accuracy, precision, recall, F1-score and confidence intervals per fault class.

- Systematically evaluate classifier performance under progressively reduced gas subsets (removing one or more gases at a time) to determine the minimum gas panel that preserves acceptable diagnostic accuracy.

- Benchmark the best-performing ML model directly against the conventional methods from Objective 1, on the same held-out test data.

- Develop a REST API (FastAPI) serving the validated model with a locked, versioned preprocessing pipeline to guarantee training–inference consistency.

- Develop a MATLAB client — including an illustrative Simulink transformer model providing electrical operating context (voltage, current, load, temperature) — that consumes the API, explicitly without using Simulink to generate or infer gas concentrations unless independently validated against a peer-reviewed gas-generation model.

# 5. Scope and Boundaries

Core scope (the research the thesis is judged on)

Objectives 1–7: the DGA data-science and machine-learning diagnostic framework, including the reduced-gas-subset investigation and the benchmark against conventional methods. This is the deliverable that must be completed to a rigorous standard.

Extension / demonstration scope

Objective 8: the MATLAB/Simulink integration and client dashboard. This has genuine engineering and demonstration value for the client-facing deliverable, but it is not the basis on which the research contribution is judged — protecting the project timeline if integration work runs longer than planned.

# 6. Significance

- Gives utilities and asset managers a quantified basis for deciding between full laboratory gas chromatography and cheaper reduced-gas online monitors.

- Produces a reproducible, properly validated ML-vs-conventional-method benchmark — a comparison often asserted in the literature but rarely demonstrated with rigorous statistical validation.

- Delivers a working prototype diagnostic architecture (model + API + engineering client), not only an offline analysis notebook.

# 7. Methodological Safeguards

The following safeguards are built into the methodology from the outset, to ensure the work withstands review scrutiny:

- Ground-truth provenance will be explicitly documented — dataset fault labels must originate independently of the conventional interpretation methods being benchmarked, to avoid circular validation.

- Scaler and feature-selection parameters will be fitted only on training folds and applied unchanged to test data and live inference (no train/test leakage).

- Model evaluation will use stratified k-fold cross-validation with reported confidence intervals — not a single train/test split — to responsibly handle the modest size of public DGA datasets.

- Reduced-gas-subset experiments will be run as controlled ablations on the same folds as the full-panel baseline, isolating gas availability as the only varying factor.

- The Simulink transformer model is explicitly scoped to provide electrical operating context only. It will not be used to generate or approximate gas-concentration data unless a literature-validated, citable gas-generation model is developed as a separate, clearly labeled extension.

# 8. Anticipated Limitations and Mitigations

| Limitation | Mitigation |
| --- | --- |
| Public DGA datasets are relatively small and class-imbalanced. | Stratified k-fold cross-validation, class-balancing techniques, and results reported with confidence intervals rather than single point-estimate accuracy. |
| Reduced-gas ablations could be confounded by other preprocessing choices. | Reduced-gas models trained and evaluated on identical folds/pipeline as the full-panel baseline, changing only gas availability. |
| Simulink/API integration is engineering work, not new diagnostic findings. | Explicitly scoped as an extension/demonstration layer (Section 5), not counted as the thesis's core contribution. |
| Risk of scope creep across three integrated subsystems. | Core deliverable (Objectives 1–7) is fully self-contained and defensible even if the MATLAB/Simulink extension is reduced in depth. |

# 9. Summary Statement

This project investigates whether machine learning can reliably diagnose incipient power-transformer faults from Dissolved Gas Analysis under realistic, reduced-gas-panel conditions, benchmarked rigorously against established conventional interpretation standards — and demonstrates the resulting model in a practical MATLAB/Simulink–Python engineering architecture, with an explicit, documented boundary between simulated electrical context and empirically sourced chemical diagnostic data.