Project Roadmap - Version 3

Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning

Step-by-step plan: what is done, in which order, and in which working environment

MPhil Thesis, University of Mines and Technology (UMaT), Tarkwa

Supervisor: Prof. John Annan

Prepared: 9 October 2026; updated 10 October 2026 (figure numbers and shared plot style added); Version 3, 12 October 2026: Study 2, an exploratory improvement study, added as Steps 31A to 31F (decision D28)

# 1. How to read this roadmap

The whole project is carried out in three working environments. Every step in this roadmap is labelled with the one environment in which it is done. The steps are numbered from 1 to 45 and are done one after the other, in that order. A step starts only when the step before it has passed its check. Version 3 adds Study 2 (Steps 31A to 31F), done between Steps 31 and 32 after the confirmatory results; it has its own protocol, written before any Study 2 model was trained.

The four labels used throughout are:

[CLAUDE CODE]  Python coding, data preparation, machine learning and statistics - done here, in this Claude Code chat.

[MATLAB AGENTIC TOOLKIT]  MATLAB programming - done with the MATLAB Agentic Toolkit.

[SIMULINK AGENTIC TOOLKIT]  Simulink and Simscape block modelling - done with the Simulink Agentic Toolkit.

[APPROVAL GATE]  A decision or approval by you and Prof. Annan that no tool can make.

Every step is written in the same way:

•  Input - the files the step needs and the guide section to follow.

•  Do - what is done, in plain words.

•  Output - the files the step produces and where they are saved.

•  Check - the test the step must pass before the next step starts.

•  Tell the toolkit - for MATLAB and Simulink steps only: a short instruction to hand to the MATLAB or Simulink Agentic Toolkit.

The results we expect, the statistical tests, every formula (with the meaning of each symbol) and every graph to be drawn are set out in the companion document Expected_Results_and_Analysis_Plan.docx. That document is approved in Step 4, before any analysis is run. Table and figure numbers in this roadmap refer to that document.

# 2. The three working environments

Each environment has a clear job. No environment does the job of another, so there is never any doubt about where a piece of work belongs.

| Environment | What is done there | Main tools | Folders it writes to |
| --- | --- | --- | --- |
| CLAUDE CODE (this chat) | Data preparation; all Python code; machine learning; reduced-gas study; statistical analysis; FastAPI service; result tables and figures; Word documents and thesis drafting. | Python 3, pandas, scikit-learn, XGBoost, SciPy, statsmodels, SHAP, FastAPI, pytest | 02_Standards (tables), 03_Data, 06_Python_ML, 07_Experiments, 08_Statistical_Analysis, 09_API_FastAPI, 11_Results, 12_Thesis, 13_Publication |
| MATLAB AGENTIC TOOLKIT | All MATLAB programming: the Rogers, IEC 60599 and Duval Triangle methods; their unit tests; Duval Triangle plots; the App Designer dashboard; the MATLAB client that calls the FastAPI service; the end-to-end test-bench run. | MATLAB R2025b, matlab.unittest, App Designer, webwrite / webread | 04_MATLAB_Conventional, 10_Dashboard_Client, 11_Results/conventional |
| SIMULINK AGENTIC TOOLKIT | All Simulink and Simscape block modelling: the seven-subsystem transformer operating model, model checks, verification against IEC 60076-7, scenario runs, the DGA sampling-event subsystem, and linking the model to the dashboard. | Simulink, Simscape, Simscape Electrical, Model Advisor, Simulation Data Inspector | 05_Simulink_Model |
| APPROVAL GATE (you and Prof. Annan) | Decisions and approvals that no tool can make. | - | 00_Project_Admin |

Number of steps in each environment: Claude Code 28, MATLAB Agentic Toolkit 8, Simulink Agentic Toolkit 7, approval gates 2.

# 3. How the three environments stay in sync

The three environments do not share memory; they share files. Every hand-over file has one owner (the only environment allowed to write it) and one or more readers. Nothing is passed by copy and paste. Five rules hold for every file:

1.  One record identifier, record_id, is used in every file.

2.  One gas order and one unit: H2, CH4, C2H6, C2H4, C2H2, in ppm.

3.  One fault-class code: 0 Normal, 1 PD, 2 D1, 3 D2, 4 T1, 5 T2, 6 T3, taken from label_map.csv.

4.  No number is typed by hand into code: decision limits come from 02_Standards and model parameters from params_transformer.m.

5.  Every new version of a hand-over file is recorded in CHANGELOG.md with its date and SHA-256 hash.

The hand-over files

| Hand-over file | Written by | Read by | Contents |
| --- | --- | --- | --- |
| 03_Data/processed/label_map.csv | Claude Code, Step 7 | MATLAB, Python | Original label to shared class code, with the reason |
| 03_Data/processed/dga_master.csv | Claude Code, Step 9 | MATLAB, Simulink, Python | record_id, source, five gases (ppm), true class, data role |
| 03_Data/processed/folds.csv | Claude Code, Step 10 | Python | record_id, outer fold, repeat, random seed |
| 11_Results/figures/plot_style.csv | Claude Code, Step 13 | MATLAB, Simulink, Python | Fixed colour and marker shape for every fault class and method, so all figures match |
| 02_Standards/*.csv | Claude Code, Step 12 | MATLAB, Python | Ratio limits, Duval zones, typical gas values and worked examples, each with clause and page |
| 11_Results/conventional/conventional_predictions.csv | MATLAB, Step 16 | Python | record_id, method, diagnosis or ND, ratios, boundary distance |
| 11_Results/ml/ml_predictions.csv | Claude Code, Step 22 | Python, MATLAB | record_id, model, predicted class, class probabilities |
| 06_Python_ML/models/dga_model_v1.joblib | Claude Code, Step 24 | FastAPI service | Preprocessing and model in one file, with its hash |
| 11_Results/reduced_gas/reduced_gas_subsets.csv | Claude Code, Step 25 | MATLAB | The list of gas subsets tested |
| 11_Results/conventional/conventional_applicability.csv | MATLAB, Step 26 | Python | Which method still gives a diagnosis when gases are removed |
| 05_Simulink_Model/results/sim_*.mat | Simulink, Step 36 | MATLAB dashboard | Load, temperature and ageing time series |
| 09_API_FastAPI/openapi.json | Claude Code, Step 38 | MATLAB dashboard | Request and response format of the service |
| 10_Dashboard_Client/logs/testbench_log.csv | MATLAB, Step 41 | Python | Every diagnosis made by the integrated system, with response time |

# 4. All 45 steps at a glance (plus Study 2, Steps 31A to 31F)

| Step | Environment | What is done | Main output |
| --- | --- | --- | --- |
| 1 | Claude Code | Set up the Python environment | requirements.txt |
| 2 | MATLAB toolkit | Connect the MATLAB Agentic Toolkit | MATLAB environment log |
| 3 | Simulink toolkit | Connect the Simulink Agentic Toolkit; re-run the baseline | Verification log |
| 4 | Approval gate | Approve decisions D1-D7 and the Analysis Plan | Signed checklist |
| 5 | Claude Code | Load and standardise the raw datasets | Standardised tables |
| 6 | Claude Code | Record the missing values | Missing-value report |
| 7 | Claude Code | Harmonise the fault labels | label_map.csv |
| 8 | Claude Code | Apply the scope filter | Exclusion log |
| 9 | Claude Code | Remove duplicates and audit leakage | dga_master.csv |
| 10 | Claude Code | Assign data roles and fix the folds | folds.csv |
| 11 | Claude Code | Describe the data | Tables 4.1-4.2; Figs 4.1-4.3 |
| 12 | Claude Code | Transcribe the standards' decision tables | 02_Standards CSV files |
| 13 | Claude Code | Freeze the data (version 1.0) | Hashes; Fig 3.2; plot_style.csv |
| 14 | MATLAB toolkit | Complete the conventional-method functions | Updated .m functions |
| 15 | MATLAB toolkit | Unit-test the conventional methods | Passing test log |
| 16 | MATLAB toolkit | Run the three methods on every record | conventional_predictions.csv |
| 17 | MATLAB toolkit | Plot the Duval Triangles | Figure 4.4 |
| 18 | Claude Code | Cross-check MATLAB against Python | 100 % agreement report |
| 19 | Claude Code | Build the preprocessing and feature pipelines | Pipeline code + tests |
| 20 | Claude Code | Train and tune the classifiers (nested CV) | Experiment folders |
| 21 | Claude Code | Select the final model by the written rule | Selection note |
| 22 | Claude Code | Fit the final model; predict the test sets once | ml_predictions.csv |
| 23 | Claude Code | Explain the model | Figs 4.14-4.15 |
| 24 | Claude Code | Save the versioned model | dga_model_v1.joblib |
| 25 | Claude Code | Retrain on every gas subset | reduced_gas_results.csv |
| 26 | MATLAB toolkit | Run the conventional methods with gases removed | conventional_applicability.csv |
| 27 | Claude Code | Find the minimum gas panel | Table 4.9; Figs 4.16-4.17 |
| 28 | Claude Code | Merge all predictions | merged_predictions.csv |
| 29 | Claude Code | Compute performance measures with 95 % CIs | Tables 4.3-4.5; Figs 4.5, 4.8 |
| 30 | Claude Code | Run the significance tests | Tables 4.6-4.7; Figs 4.7, 4.11 |
| 31 | Claude Code | Test the boundary hypothesis | Table 4.8; Fig 4.12 |
| 31A | Claude Code | Study 2: pre-register Study 2 (exploratory improvement study) | Study2_Protocol.docx |
| 31B | Claude Code | Study 2: build the pooled, deduplicated data set | study2_pooled.csv |
| 31C | Claude Code | Study 2: leave-one-source-out training and prediction | 07_Experiments study2_loso |
| 31D | Claude Code | Study 2: measures, paired contrasts and reject option | Tables 4.12-4.13; Figs 4.23-4.24 |
| 31E | Claude Code | Study 2: interpret Study 2 against its decision rules | Study 2 report |
| 31F | Claude Code | Study 2: search for a fresh confirmation data set | study2_confirmation_search.md |
| 32 | Claude Code | Generate all Chapter 4 tables and figures | Figs 4.6, 4.9, 4.10, 4.13 |
| 33 | Simulink toolkit | Rebuild the transformer operating model | Model .slx; Fig 3.4 |
| 34 | Simulink toolkit | Run the model checks | Model Advisor report |
| 35 | Simulink toolkit | Verify against IEC 60076-7 | Table 4.10; Fig 4.18 |
| 36 | Simulink toolkit | Run the operating scenarios | sim_*.mat; Fig 4.19 |
| 37 | Simulink toolkit | Add the DGA sampling-event subsystem | Updated model |
| 38 | Claude Code | Build the FastAPI service | Service + openapi.json |
| 39 | MATLAB toolkit | Build the App Designer dashboard | DGADashboard.mlapp; Fig 4.22 |
| 40 | Simulink toolkit | Link the Simulink model to the dashboard | Working test bench |
| 41 | MATLAB toolkit | Run the end-to-end test bench | testbench_log.csv; Fig 4.20 |
| 42 | Claude Code | Evaluate fidelity and response time | Table 4.11; Fig 4.21 |
| 43 | Claude Code | Write Chapters 3 to 5 | Chapters; Figs 3.1, 3.3 |
| 44 | Claude Code | Prepare the journal manuscript | Manuscript |
| 45 | Approval gate | Supervisor review and approval | Approved draft |

# 5. The steps in detail

## Stage A - Setting up (Steps 1 to 4)

Step 01  [CLAUDE CODE]  Set up the Python environment

Input: This computer (Python is not installed yet).

Do: Install Python 3.12 (64-bit). Create a virtual environment in 06_Python_ML/.venv. Install the libraries with fixed versions: pandas, numpy, scikit-learn, xgboost, scipy, statsmodels, shap, matplotlib, openpyxl, fastapi, uvicorn, pydantic, pytest and joblib. Save the exact versions.

Output: 06_Python_ML/requirements.txt; an environment note in CHANGELOG.md.

Check: A short test imports every library without error and the versions are recorded.

Step 02  [MATLAB AGENTIC TOOLKIT]  Connect the MATLAB Agentic Toolkit

Input: MATLAB R2025b; project_setup.m; MATLAB Build Guide, Part A1.

Do: Connect the toolkit to MATLAB, run project_setup.m and list the installed toolboxes. Make sure drive C: has free space, because MATLAB stops recording results when C: is full.

Output: 00_Project_Admin/environment_matlab.txt (MATLAB version and toolboxes).

Check: MATLAB answers a test command; Statistics and Machine Learning Toolbox, Simulink, Simscape and Simscape Electrical are listed.

Tell the toolkit: Run project_setup.m, then run ver and save the output to 00_Project_Admin/environment_matlab.txt.

Step 03  [SIMULINK AGENTIC TOOLKIT]  Connect the Simulink Agentic Toolkit and re-run the baseline

Input: 05_Simulink_Model/reference_build; MATLAB Build Guide, Part B12.

Do: Connect the toolkit and run the existing verification scripts on the reference build, to confirm the model behaves exactly as on 3 October 2026.

Output: A new, dated verification log in 05_Simulink_Model/reference_build.

Check: The numbers match the log of 3 October 2026 (largest hot-spot difference 0.061 K at rated load and 0.031 K in the load-step test).

Tell the toolkit: Add the project folders to the path, run reference_build/run_verification.m and run_test2_and_figs.m, and save the printed log with today's date.

Step 04  [APPROVAL GATE]  Approve the decisions and the analysis plan

Input: decisions_log.md (D1-D7); Expected_Results_and_Analysis_Plan.docx, Section 14 (items for approval).

Do: Meet Prof. Annan. Close each decision D1-D7 and mark each item in the approval list.

Output: decisions_log.md with every decision CLOSED and dated; the approved item list.

Check: No open decision remains that affects Steps 5 to 32.

## Stage B - Data preparation (Steps 5 to 13) - Claude Code

Step 05  [CLAUDE CODE]  Load and standardise the raw datasets

Input: 03_Data/raw: the IEC TC 10 table, the three Dissanayake files and the Li 2019 file; the data cards in 03_Data/provenance.

Do: Check each file's SHA-256 against its data card. Read the files without changing them. Give the gases the same names and order (H2, CH4, C2H6, C2H4, C2H2) and confirm the unit is ppm. Add record_id, source and the original label to every record.

Output: 03_Data/interim/*_standardised.csv.

Check: Record counts equal the data cards: 117; 584, 70 and 49; 201.

Step 06  [CLAUDE CODE]  Record the missing values

Input: The standardised tables; the missing-value rule approved in Step 4.

Do: Mark every blank or dash as missing, never as zero. Count missing values per gas and per source. Apply the approved rule.

Output: 03_Data/interim/missing_values_report.csv.

Check: Every missing value is counted and none has been silently filled.

Step 07  [CLAUDE CODE]  Harmonise the fault labels

Input: The standardised tables; the decisions on the Normal class, the T1/T2 cases and the Li 2019 labels (Step 4).

Do: Build one table that turns every original label into the shared code 0-6. Dissanayake codes are used as given. IEC TC 10: PD to 1, D1 to 2, D2 to 3, T3 to 6, and the combined T1/T2 cases follow the approved rule. Li 2019 text labels follow the approved mapping. Every row states its reason.

Output: 03_Data/processed/label_map.csv.

Check: Every original label maps to exactly one code, or is excluded with a written reason.

Step 08  [CLAUDE CODE]  Apply the scope filter

Input: IEC TC 10 equipment codes (P, U, R, I, B, C, S); the approved scope decision.

Do: Keep the equipment types approved in Step 4 (proposed: power transformers P and U only). Record every excluded record and why.

Output: 03_Data/interim/exclusion_log.csv.

Check: Counts per class before and after the filter are recorded.

Step 09  [CLAUDE CODE]  Remove duplicates and audit leakage

Input: All standardised and filtered tables.

Do: Find records with identical gas values within and across sources - in particular the 49-row IEC file of the Dissanayake dataset against the 117 IEC TC 10 cases, and the Dissanayake training file against its test file. Remove from the training data any record that also appears in a test set. Write the clean master table.

Output: 03_Data/interim/duplicate_report.csv; 03_Data/processed/dga_master.csv.

Check: An automated test confirms that no gas record appears in two different data roles.

Step 10  [CLAUDE CODE]  Assign data roles and fix the folds

Input: dga_master.csv.

Do: Give every record one role: development set (Dissanayake training data after cleaning), internal test set (Dissanayake unseen test file), independent benchmark (IEC TC 10, inspection-confirmed) and external test (Li 2019, sensitivity analysis only). Create the repeated stratified cross-validation folds on the development set with one fixed random seed.

Output: 03_Data/processed/folds.csv, with the seed written in the file.

Check: Roles do not overlap and every fold keeps the class proportions.

Step 11  [CLAUDE CODE]  Describe the data

Input: dga_master.csv.

Do: Produce class counts, gas medians and interquartile ranges per class, and the Kruskal-Wallis test per gas (Analysis Plan, Section 6.3).

Output: 11_Results/tables: Tables 4.1 and 4.2; 11_Results/figures: Figures 4.1 to 4.3 (Analysis Plan, Section 12.4).

Check: The tables are produced by script only; no number is typed by hand.

Step 12  [CLAUDE CODE]  Transcribe the standards' decision tables

Input: Copies of IEC 60599, IEEE C57.104-2019 and the Duval Triangle 1 zone definitions (to be obtained).

Do: Transcribe the IEC ratio code limits, the Rogers table, the Duval Triangle 1 zone vertices, the typical (normal) gas values and the worked examples printed in the standards into CSV files, each row with clause and page. Transcribe twice and compare; then you spot-check against the standard, as was done for the IEC TC 10 data.

Output: 02_Standards: iec_ratio_table.csv, rogers_ratio_table.csv, duval_triangle_zones.csv, typical_values.csv, worked_examples.csv.

Check: Both transcriptions are identical and your spot-check passes.

Step 13  [CLAUDE CODE]  Freeze the data (version 1.0)

Input: All files from Steps 5 to 12.

Do: Record the SHA-256 of every processed file and standards table in CHANGELOG.md. From now on these files change only through a new, recorded version.

Output: Data version 1.0; Figure 3.2 (data-preparation flow with counts); 11_Results/figures/plot_style.csv with the fixed colour and marker shape of every class and method (Analysis Plan, Section 12.2).

Check: Hashes recorded; all later stages read only these files.

## Stage C - Conventional DGA methods (Steps 14 to 17) - MATLAB Agentic Toolkit

Step 14  [MATLAB AGENTIC TOOLKIT]  Complete the conventional-method functions

Input: 04_MATLAB_Conventional (gas_ratios.m, duval_xy.m, conventional_diagnosis.m); the 02_Standards tables; MATLAB Build Guide, Part A6.

Do: Extend the functions so that they read every limit from 02_Standards; return Normal when all gases are below their typical values (normality gate); return ND (no diagnosis) when no rule applies or a needed gas is missing; compute each sample's distance to the nearest decision boundary; and process a whole table in one call.

Output: Updated functions in 04_MATLAB_Conventional.

Check: No threshold is typed in the code; every value is read from 02_Standards.

Tell the toolkit: Extend conventional_diagnosis.m with a normality gate from typical_values.csv, ND handling and boundary distances as defined in the Analysis Plan, Sections 4.3 to 4.5, and add a batch function that reads dga_master.csv.

Step 15  [MATLAB AGENTIC TOOLKIT]  Unit-test the conventional methods

Input: 02_Standards/worked_examples.csv.

Do: Write matlab.unittest tests: the published worked examples, zero denominators, missing gases, and points lying exactly on a boundary.

Output: 04_MATLAB_Conventional/tests and a test log.

Check: runtests reports that every test passes.

Tell the toolkit: Create a matlab.unittest test class for the conventional methods from worked_examples.csv plus the edge cases listed, and run runtests.

Step 16  [MATLAB AGENTIC TOOLKIT]  Run the three methods on every record

Input: 03_Data/processed/dga_master.csv.

Do: Run Rogers, IEC 60599 and Duval Triangle on every record. Keep the ND results; never remove them.

Output: 11_Results/conventional/conventional_predictions.csv.

Check: One row per record and method; the number of ND results is reported.

Tell the toolkit: Run the batch conventional diagnosis on dga_master.csv and write conventional_predictions.csv with the columns given in the roadmap, Section 3.

Step 17  [MATLAB AGENTIC TOOLKIT]  Plot the Duval Triangles

Input: conventional_predictions.csv; duval_triangle_zones.csv.

Do: Plot Duval Triangle 1 for each data role, with the zones drawn from the CSV file and each sample coloured and shaped by its true class, using the colours and markers in plot_style.csv.

Output: Figure 4.4: 11_Results/figures/duval_*.png and .pdf, with the plotted data saved as CSV.

Check: Zone polygons match the standard; the figures are made by script.

Tell the toolkit: Use plot_duval_triangle.m to save one figure per data role in 11_Results/figures.

## Stage D - Machine learning (Steps 18 to 24) - Claude Code

Step 18  [CLAUDE CODE]  Cross-check MATLAB against Python

Input: conventional_predictions.csv; the 02_Standards tables.

Do: Re-implement the three conventional methods in Python, reading the same tables, and compare the results with MATLAB's.

Output: 08_Statistical_Analysis/cross_language_check.csv.

Check: Identical diagnoses on 100 % of records, and ratios equal to within 1e-9.

Step 19  [CLAUDE CODE]  Build the preprocessing and feature pipelines

Input: dga_master.csv; folds.csv.

Do: Build scikit-learn pipelines for the four feature sets of the Analysis Plan (Section 5.1). Scaling, class weighting and any oversampling are fitted inside the training folds only.

Output: 06_Python_ML/src and 06_Python_ML/configs.

Check: pytest passes, including a leakage test proving that the scaler sees training rows only.

Step 20  [CLAUDE CODE]  Train and tune the classifiers (nested cross-validation)

Input: The pipelines; folds.csv.

Do: Train the five approved classifiers (SVM, Random Forest, XGBoost, neural network and the approved fifth model) and a majority-class baseline. The inner loop tunes the settings; the outer loop measures performance. Save every run with its configuration and seed.

Output: 07_Experiments/<date>_<run>/ (configuration, seed, metrics, fold predictions).

Check: Re-running a saved configuration gives the same numbers.

Step 21  [CLAUDE CODE]  Select the final model by the written rule

Input: The cross-validation results.

Do: Apply the rule fixed in the Analysis Plan: the highest mean outer-fold macro-F1; if the best and the next model are not significantly different, the simpler one is chosen.

Output: 07_Experiments/model_selection.md.

Check: The choice follows the written rule and is made before any test set is opened.

Step 22  [CLAUDE CODE]  Fit the final model and predict the test sets once

Input: The selected pipeline; the development set; the three test sets.

Do: Tune and fit the selected pipeline on the whole development set. Predict the internal test set, the IEC TC 10 benchmark and the Li 2019 external set, once.

Output: 11_Results/ml/ml_predictions.csv.

Check: A log shows that the test sets were opened only in this step.

Step 23  [CLAUDE CODE]  Explain the model

Input: The fitted model; ml_predictions.csv.

Do: Compute permutation importance and SHAP values and rank the gases and ratios (Analysis Plan, Section 8.1).

Output: Importance tables; Figures 4.14 (permutation importance) and 4.15 (SHAP summary).

Check: Results are reported as found, including any that differ from engineering experience.

Step 24  [CLAUDE CODE]  Save the versioned model

Input: The fitted pipeline.

Do: Save the preprocessing and the model together in one file, with its SHA-256 and a short model card (data version, settings, metrics).

Output: 06_Python_ML/models/dga_model_v1.joblib and model_card.md.

Check: Reloading the file reproduces the predictions of Step 22 exactly.

## Stage E - Reduced-gas study (Steps 25 to 27) - Claude Code and MATLAB Agentic Toolkit

Step 25  [CLAUDE CODE]  Retrain on every gas subset

Input: The pipelines; folds.csv.

Do: Repeat Steps 19 and 20 with gases removed: all 31 non-empty subsets of the five gases, plus panels that match common online monitors (to be listed from the literature review). Same folds and same pipeline; only the available gases change.

Output: 11_Results/reduced_gas/reduced_gas_results.csv and reduced_gas_subsets.csv.

Check: Every subset uses the identical folds of Step 10.

Step 26  [MATLAB AGENTIC TOOLKIT]  Run the conventional methods with gases removed

Input: dga_master.csv; reduced_gas_subsets.csv.

Do: For each subset, set the removed gases to missing and run the three methods, to show which method can still give a diagnosis.

Output: 11_Results/conventional/conventional_applicability.csv.

Check: A method that needs a removed gas returns ND, never a guess.

Tell the toolkit: For each subset in reduced_gas_subsets.csv, set the removed gases to NaN, run the batch diagnosis and save the share of ND per method in conventional_applicability.csv.

Step 27  [CLAUDE CODE]  Find the minimum gas panel

Input: reduced_gas_results.csv; conventional_applicability.csv.

Do: For each subset, compute the loss in macro-F1 against the full panel with its 95 % confidence interval, and find the smallest panel whose loss stays within the tolerance approved in Step 4 (Analysis Plan, Section 8).

Output: Table 4.9; Figures 4.16 (accuracy against number of gases) and 4.17 (gas-subset matrix).

Check: The tolerance used is the one written down before the results were seen.

## Stage F - Comparison and statistics (Steps 28 to 32, with Study 2 in Steps 31A to 31F) - Claude Code

Step 28  [CLAUDE CODE]  Merge all predictions

Input: dga_master.csv; conventional_predictions.csv; ml_predictions.csv.

Do: Join the true classes, the conventional predictions and the ML predictions on record_id.

Output: 08_Statistical_Analysis/merged_predictions.csv.

Check: No record is lost or duplicated in the join.

Step 29  [CLAUDE CODE]  Compute the performance measures with 95 % confidence intervals

Input: merged_predictions.csv.

Do: Compute strict and conditional accuracy, coverage, per-class precision, recall and F1, macro-F1, balanced accuracy, Cohen's kappa and MCC, with Wilson and bootstrap confidence intervals (Analysis Plan, Sections 4.3 and 6).

Output: Tables 4.3 to 4.5; Figures 4.5 and 4.8 (confusion matrices).

Check: Every number comes from the merged file of Step 28.

Step 30  [CLAUDE CODE]  Run the significance tests

Input: Cross-validation results; merged_predictions.csv.

Do: Friedman and Nemenyi tests for the classifiers; Cochran's Q, then McNemar tests with Holm correction, for ML against each conventional method; Cohen's kappa between every pair of methods (Analysis Plan, Section 7).

Output: Tables 4.6 and 4.7; Figures 4.7 (critical-difference diagram) and 4.11 (kappa heatmap).

Check: Every test is reported with its exact p-value and effect size, significant or not.

Step 31  [CLAUDE CODE]  Test the boundary hypothesis

Input: merged_predictions.csv (with boundary distances).

Do: Fit a logistic regression of disagreement (ML different from conventional) on the distance to the nearest boundary, for each conventional method (Analysis Plan, Section 7.6).

Output: Table 4.8; Figure 4.12 (disagreement against boundary distance).

Check: Odds ratio and 95 % confidence interval reported; the result is stated as found.

Study 2 - exploratory improvement study (Steps 31A to 31F, decision D28). Added in Version 3 after the confirmatory results; protocol: 00_Project_Admin/Study2_Protocol.docx. The confirmatory results of Steps 22-31 are not changed.

Step 31A  [CLAUDE CODE]  Pre-register Study 2 (exploratory improvement study)

Input: The confirmatory results of Steps 22-31; decisions_log.md.

Do: Write the Study 2 protocol before any Study 2 model is trained: questions, data rules, models A (released), B (pooled) and C (hybrid), measures, statistics, reject option and decision rules (decision D28). Record its SHA-256.

Output: 00_Project_Admin/Study2_Protocol.docx; 03_Data/study2/study2_protocol.sha256.

Check: The protocol fingerprint is dated before the first Study 2 model; the confirmatory results stay unchanged.

Step 31B  [CLAUDE CODE]  Build the pooled, deduplicated data set

Input: dga_master.csv; conventional_predictions.csv; Study 2 protocol.

Do: Remove exact copies across sources by the fixed priority; form near-duplicate groups over all pooled records (Step 10 rule); merge T1 and T2; add the hybrid inputs (conventional answers, gate flags, boundary distances).

Output: 03_Data/study2/study2_pooled.csv with its SHA-256 manifest; table of records per source and class.

Check: No exact copy left across sources; every label conflict listed; data version 1.0 unchanged.

Step 31C  [CLAUDE CODE]  Leave-one-source-out training and prediction

Input: study2_pooled.csv; ml_config.yaml; dga_model_v1.

Do: Hold out each of the four sources in turn; train and tune models B and C on the other sources only (near-copies of held-out records removed from training); predict the held-out source once; apply model A unchanged.

Output: 07_Experiments/<date>_study2_loso/ (configuration, seeds, predictions and probabilities).

Check: No held-out record or near-copy in any training set; re-running a saved task gives identical predictions.

Step 31D  [CLAUDE CODE]  Measures, paired contrasts and reject option

Input: The Study 2 predictions; conventional answers of the same records.

Do: Macro-F1, strict and balanced accuracy with Wilson and bootstrap intervals; contrasts B-A, C-B and C against the best conventional method (bootstrap, McNemar with Holm); accuracy at the coverage of IEC 60599 and Rogers (Chow 1970).

Output: Tables 4.12 (results by held-out source) and 4.13 (contrasts and reject option); Figures 4.23 (macro-F1 by held-out source and model) and 4.24 (accuracy against coverage).

Check: Every number comes from the saved Study 2 predictions; all results labelled exploratory.

Step 31E  [CLAUDE CODE]  Interpret Study 2 against its decision rules

Input: Tables 4.12-4.13; the protocol.

Do: Apply the three pre-registered decision rules exactly as written and state what Study 2 shows and does not show, beside the confirmatory results.

Output: Study 2 report; 08_Statistical_Analysis/study2_decisions.json.

Check: Each decision follows the written rule; no confirmatory result is changed.

Step 31F  [CLAUDE CODE]  Search for a fresh confirmation data set

Input: Literature review; data cards.

Do: Search legitimate sources (journals, standards bodies, open repositories with a stated licence) for inspection-confirmed DGA cases not used so far; record each candidate, its licence and its overlap with the data already used. No data from pirated or unlicensed copies.

Output: 03_Data/provenance/study2_confirmation_search.md.

Check: Every candidate has a citation and a licence statement; overlaps checked.

Step 32  [CLAUDE CODE]  Generate all Chapter 4 tables and figures

Input: All result files.

Do: Run one script that rebuilds every Chapter 4 table and figure from the saved files, including Figures 4.6, 4.9, 4.10 and 4.13, following the style rules of Analysis Plan Section 12.2. The Study 2 tables and figures (Tables 4.12-4.13, Figures 4.23-4.24) are rebuilt the same way, in their own section labelled exploratory.

Output: 11_Results/tables and 11_Results/figures.

Check: Deleting 11_Results and running the script again gives identical files.

## Stage G - Simulink operating model (Steps 33 to 37) - Simulink Agentic Toolkit

Step 33  [SIMULINK AGENTIC TOOLKIT]  Rebuild the transformer operating model

Input: MATLAB Build Guide, Part B (B1 to B11); params_transformer.m; the reference-build diagrams.

Do: Build Transformer_Operating_Model.slx with pure Simscape blocks: SS1 grid supply, SS2 40 MVA transformer, SS3 LV measurement, SS4 variable load, SS5 losses to heat, SS6 thermal network, SS7 outputs and ageing. Every block reads its values from params_transformer.m and every subsystem carries an annotation.

Output: 05_Simulink_Model/Transformer_Operating_Model.slx; Figure 3.4 (top-level model screenshot).

Check: The model updates without errors and its structure matches the reference-build diagrams.

Tell the toolkit: Build Transformer_Operating_Model.slx following MATLAB_Build_Guide Part B, sections B2 to B11, using only variables from params_transformer.m, and add an annotation to each subsystem.

Step 34  [SIMULINK AGENTIC TOOLKIT]  Run the model checks

Input: The new model; MATLAB Build Guide, Part D1.

Do: Run Model Advisor and the checks listed in Part D1. Fix every reported issue, or record why it is accepted.

Output: 05_Simulink_Model/checks/model_advisor_report.

Check: No unresolved errors remain.

Tell the toolkit: Run Model Advisor on Transformer_Operating_Model.slx, fix the reported issues and save the report.

Step 35  [SIMULINK AGENTIC TOOLKIT]  Verify against IEC 60076-7

Input: The model; the verification method of Build Guide Part B12.

Do: Compare the model with an independent solution of the IEC 60076-7 equations at rated load and in a load step from about 0.6 to 1.2 per unit (Analysis Plan, Section 9).

Output: Verification log in 05_Simulink_Model/results; Table 4.10; Figure 4.18.

Check: The largest temperature difference is within the approved tolerance (proposed 0.1 K) and the top-oil 63 % rise time equals k11 times the oil time constant.

Tell the toolkit: Run the verification of Build Guide Part B12 on the new model and save the log and figure with today's date.

Step 36  [SIMULINK AGENTIC TOOLKIT]  Run the operating scenarios

Input: The verified model; the approved scenarios.

Do: Write the approved scenarios in scenarios.m (proposed: constant rated load, a daily load cycle and a short overload). Simulate each one and log the load, the top-oil and hot-spot temperatures and the ageing in the Simulation Data Inspector.

Output: 05_Simulink_Model/results/sim_*.mat; Figure 4.19 (one per scenario).

Check: Each run can be reproduced from params_transformer.m and scenarios.m.

Tell the toolkit: Create scenarios.m with the three approved load profiles, run each one, log the SS7 outputs to the Simulation Data Inspector and save sim_<scenario>.mat.

Step 37  [SIMULINK AGENTIC TOOLKIT]  Add the DGA sampling-event subsystem

Input: dga_master.csv (held-out records); sampling times added to params_transformer.m.

Do: Add a subsystem that, at the set sampling times, outputs the record_id of the next real held-out record. It never computes or changes a gas value; the gases are read from the record by the dashboard.

Output: The model with the sampling-event subsystem.

Check: No block in the model produces a gas concentration (inspection plus a test).

Tell the toolkit: Add a sampling-event subsystem that outputs record_id at the sampling times in params_transformer.m; it must not output any gas value.

## Stage H - Integration and test bench (Steps 38 to 42) - all three environments

Step 38  [CLAUDE CODE]  Build the FastAPI service

Input: dga_model_v1.joblib.

Do: Build the service: POST /diagnose takes the five gases and returns the ML class, the class probabilities and the model version; GET /health reports that the service is alive. Inputs are validated (five non-negative numbers). Write pytest tests and publish openapi.json.

Output: 09_API_FastAPI: service, tests, openapi.json.

Check: All tests pass and the service runs on the project laptop.

Step 39  [MATLAB AGENTIC TOOLKIT]  Build the App Designer dashboard

Input: MATLAB Build Guide, Part C (C1 to C6); openapi.json.

Do: Build DGADashboard.mlapp: load a record; show the three conventional diagnoses computed in MATLAB; call the service with webwrite for the ML diagnosis; plot the sample in the Duval Triangle; show the agreement flag and the operating context.

Output: 10_Dashboard_Client/DGADashboard.mlapp; Figure 4.22 (annotated screenshot).

Check: Three known records (one per fault family) give the same answers as the offline results.

Tell the toolkit: Build DGADashboard.mlapp following MATLAB_Build_Guide Part C and connect the Diagnose button to the /diagnose endpoint described in openapi.json.

Step 40  [SIMULINK AGENTIC TOOLKIT]  Link the Simulink model to the dashboard

Input: The model with sampling events; the dashboard.

Do: Let the dashboard run the model (Run Simulation button) and use the sampling events to trigger the diagnosis of the next record.

Output: The updated model and app: a working test bench.

Check: A full simulated day runs from the app without error.

Tell the toolkit: Connect RunSimulationButtonPushed to sim of Transformer_Operating_Model and pass the sampling-event record_id values to the dashboard.

Step 41  [MATLAB AGENTIC TOOLKIT]  Run the end-to-end test bench

Input: The working test bench; the held-out records.

Do: Run the integrated system over every held-out record and log each diagnosis and its response time.

Output: 10_Dashboard_Client/logs/testbench_log.csv; Figure 4.20 (test-bench run).

Check: One log row per record and no failed calls.

Tell the toolkit: Run the test-bench script over all records whose role is internal test or benchmark and write testbench_log.csv.

Step 42  [CLAUDE CODE]  Evaluate fidelity and response time

Input: testbench_log.csv; ml_predictions.csv; conventional_predictions.csv.

Do: Compare the test-bench log with the offline predictions, and compute fidelity and the median and 95th-percentile response times (Analysis Plan, Section 10).

Output: Table 4.11; Figure 4.21 (response times); an integration report.

Check: Fidelity is 100 %; any mismatch is traced and fixed before writing starts.

## Stage I - Writing and approval (Steps 43 to 45)

Step 43  [CLAUDE CODE]  Write Chapters 3 to 5

Input: The READMEs; 11_Results.

Do: Draft the methods, results and conclusions chapters in Word (12 pt, 1.15 spacing), using only the tables and figures in 11_Results.

Output: 12_Thesis/Chapter3.docx, Chapter4.docx and Chapter5.docx; Figures 3.1 and 3.3.

Check: Every number traces to a file in 07_Experiments or 11_Results; nothing marked TO VERIFY remains.

Step 44  [CLAUDE CODE]  Prepare the journal manuscript

Input: The thesis chapters; 11_Results.

Do: Extract the core results into a journal manuscript with a reproducibility statement.

Output: 13_Publication/manuscript.docx.

Check: The reference register has no unverified entry.

Step 45  [APPROVAL GATE]  Supervisor review and approval

Input: The thesis chapters and the manuscript.

Do: Prof. Annan reviews; corrections are made and recorded.

Output: The approved thesis draft; a CHANGELOG entry.

Check: Written approval received.

# 6. Where the existing documents are used

| Document | Used in steps |
| --- | --- |
| MATLAB_Build_Guide.docx - Part A (MATLAB code and parameters) | 2, 14 |
| MATLAB_Build_Guide.docx - Part B (Simulink and Simscape model; run and verify) | 3, 33, 34, 35, 36, 37 |
| MATLAB_Build_Guide.docx - Part C (App Designer dashboard) | 39, 40, 41 |
| MATLAB_Build_Guide.docx - Part D (final checklist) | 34, 45 |
| Expected_Results_and_Analysis_Plan.docx (companion document) | 4, 6, 10, 11, 14, 19 to 31, 35, 42 |
| Project_Methodology_Plan.docx (objectives, research questions, hypothesis) | 4, 20, 29 to 31, 43 |
| Project_Overview_and_Objectives.docx (background to decisions D1 to D3) | 4 |
| decisions_log.md (decisions D1 to D7) | 4, 6, 7, 8, 20 |

# 7. Approval gates

There are two formal gates. Gate 1 (Step 4) comes before any data is prepared or analysed, so that the decisions and the analysis plan are fixed while the results are still unknown. Gate 2 (Step 45) comes before submission. The label, scope and missing-value choices made in Steps 6, 7 and 8 simply apply the answers given at Gate 1; if a new question appears during the work, the work stops at that step until it is answered and recorded in decisions_log.md. Study 2 (Steps 31A to 31F) was added after the confirmatory results at the researcher's request; it is pre-registered in its own protocol and reported as exploratory.