Showing the Transformer Simulation

A simple step-by-step guide: set it up and present it to your lecturer

Project: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

# 1. What you are showing

The simulation is a computer model of a 40 MVA, 110/20 kV power transformer working for 24 hours. It was built in MATLAB Simulink (with Simscape).

It works out four things over time:

- the load on the transformer,

- the top-oil temperature,

- the hot-spot temperature of the winding,

- how fast the insulation is ageing.

Important to say: the simulation only gives the working conditions of the transformer. It does not create or predict gas values. All gas values in this project come from real measured records.

The model file is:

05_Simulink_Model\Transformer_Operating_Model.slx

# 2. What you need on the computer

| Item | What is needed |
| --- | --- |
| MATLAB | R2025b. An older version cannot open the model. |
| MATLAB add-ons | Simulink, Simscape and Simscape Electrical |
| Internet and Python | Not needed for the simulation alone |
| Project folder | The whole project folder (not only the model file), copied to a short path such as C:\DGA_Project |

Do not put the folder in OneDrive, and do not rename the numbered folders (03_Data, 05_Simulink_Model, and so on).

# 3. Set it up (do this once, about 5 minutes)

- Copy the whole project folder to the computer, for example to C:\DGA_Project.

- Start MATLAB R2025b.

- In the MATLAB Command Window, type these two lines and press Enter after each:

cd C:\DGA_Project

project_setup

You should see this message:

Project paths added. Parameters loaded from params_transformer.m

Now check that the add-ons are installed. Type:

ver

license('test','Simscape_Electrical')

The list from ver must include Simulink, Simscape and Simscape Electrical. The second line must answer 1.

Remember: type project_setup again every time you restart MATLAB.

# 4. Run the simulation

## Way 1: open the model and press Run (best for the lecturer)

cd C:\DGA_Project

project_setup

open_system('Transformer_Operating_Model')

- The block diagram opens.

- Press the green Run button at the top. It takes about 10 seconds.

- Open the scopes, or the Data Inspector (Simulation tab), to see the curves.

## Way 2: run from code and draw the temperatures

res = run_transformer_simulation();

figure; plot(res.t_h, res.theta_oil_C, res.t_h, res.theta_hs_C); grid on

xlabel('Time (h)'); ylabel('Temperature (degC)'); legend('Top-oil','Hot-spot')

## Way 3: the three example scenarios

cd 05_Simulink_Model

run_step36

This runs three cases: (1) constant rated load, (2) a normal daily load cycle, (3) a short overload of 1.3 times rated load for 2 hours. The pictures are saved in 11_Results\figures (files starting F4_19).

| Scenario | Highest hot-spot temperature | Note |
| --- | --- | --- |
| 1. Rated load | about 100.3 °C | Normal full load |
| 2. Daily cycle | about 99.9 °C | Load changes through the day |
| 3. Short overload | about 129.0 °C | Shows the risk of overload |

These load patterns are examples chosen for the demonstration. They are not measured data.

# 5. What to explain on the diagram

The model has eight blocks (subsystems). Point to them in this order:

| Block | What it does |
| --- | --- |
| SS1 | The 110 kV power grid (the source) |
| SS2 | The 40 MVA, 110/20 kV transformer |
| SS3 | Measures the current and the load factor |
| SS4 | The load, which changes with time |
| SS5 | Turns the electrical losses into heat |
| SS6 | The thermal network: oil and winding temperatures (IEC 60076-7 equations) |
| SS7 | Calculates the hot-spot temperature and the ageing rate |
| SS8 | Marks four sampling times (6, 12, 18 and 22 hours). It gives no gas values. |

Every block has a text note on it. All numbers come from one file, 05_Simulink_Model\params_transformer.m. To change a value (for example the air temperature), edit that file, save it, and run again.

Reference result at rated load (20 °C air): top-oil 78.64 °C, hot-spot 100.28 °C, oil time constant 75 minutes.

# 6. Show that the model is correct

Type these in MATLAB:

cd 05_Simulink_Model

verify_step35

verify_step37

verify_step35 compares the model with an independent calculation of the IEC 60076-7 equations. All 15 checks should pass. verify_step37 checks the sampling block. All 10 checks should pass.

Numbers you can quote:

- Largest difference after the first 10 minutes: 0.0014 K (top-oil) and 0.0129 K (hot-spot).

- The accepted limit was 0.1 K, so the model is well inside it.

- Time to reach 63.2 % of the final temperature rise: 75.002 minutes (expected 75.000).

Saved evidence: 11_Results\tables\T4_10_simulink_verification.csv and 11_Results\figures\F4_18_simulink_verification.png.

# 7. A 5-minute talk plan

| Time | What to do |
| --- | --- |
| 30 s | Say what the model is for: working conditions of the transformer. No gas values are created. |
| 1 min | Open the model and walk through SS1 to SS8. |
| 1 min | Press Run. Show the top-oil temperature, hot-spot temperature and ageing rate. |
| 1 min | Show the overload scenario (Figure 4.19): the hot-spot reaches about 129 °C. |
| 1 min | Show the verification (Figure 4.18) and the 0.1 K limit. |
| 30 s | State the limits (Section 8). |

If the computer fails, show the saved pictures instead:

- 05_Simulink_Model\figures\Figure_3_4_top_level.png (the whole model)

- 05_Simulink_Model\figures\diag_SS… files (one picture per block)

- 11_Results\figures\F4_18… and F4_19… (verification and scenarios)

# 8. Be honest about the limits

- The check is verification (the model matches the IEC equations). It is not validation against measurements from a real transformer.

- The thermal constants come from an open-source model, and the electrical data are typical values for a 40 MVA 110/20 kV unit, not from a real nameplate. The standard IEC 60076-7:2018 was not obtained, so these values are marked TO VERIFY.

- The three load scenarios and the four sampling times are examples, not measured data.

- Some of the arithmetic sits in ordinary Simulink blocks, so the model is "Simscape networks plus Simulink arithmetic", not purely Simscape blocks.

# 9. If something goes wrong

| Problem | What to do |
| --- | --- |
| Error: Unrecognized function or variable 'params_transformer' | You did not run project_setup. Run it from the project folder and try again. |
| Simscape or Simscape Electrical not found | Install the product. Check with ver. |
| The model will not open | Your MATLAB is older than R2025b. |
| Strange cache errors | Close the model. Delete the folder 05_Simulink_Model\slprj and the .slxc files. Restart MATLAB, run project_setup. |
| Numbers differ from this guide | Someone changed params_transformer.m. Copy the original back from your USB copy. |
| Any other error | Copy the exact error text and send it to me. |

# 10. Quick summary

To show the simulation, type these three lines in MATLAB, then press Run:

cd C:\DGA_Project

project_setup

open_system('Transformer_Operating_Model')

Test everything once on the presentation computer a day or two before the meeting.