Showing the Simulation and the Dashboard

Open the file, click Run: a step-by-step guide for presenting to your lecturer

Project: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

# 1. What you are showing

There are three parts. Each one starts from a file that you open.

| Part | File to open | What it does |
| --- | --- | --- |
| A. Simulink model | 05_Simulink_Model\Transformer_Operating_Model.slx | Simulates the transformer for 24 hours: load, oil and hot-spot temperature, ageing |
| B. ML service (the Python part) | 09_API_FastAPI\Start_ML_Service.bat | Gives the machine-learning diagnosis to the dashboard. Runs in a black window. |
| C. Dashboard (the app) | 10_Dashboard_Client\DGADashboard.mlapp | Shows Rogers, IEC 60599, Duval and the ML diagnosis side by side |

All paths are inside the project folder. In this guide the project folder is C:\DGA_Project (yours may be different).

Important to say: the simulation only gives the working conditions of the transformer. It does not create or predict gas values. All gas values come from real measured records.

# 2. What you need on the computer

| Item | What is needed |
| --- | --- |
| MATLAB | R2025b. An older version cannot open the model or the app. |
| MATLAB add-ons | Simulink, Simscape and Simscape Electrical. To check: in MATLAB, Home tab > Add-Ons > Manage Add-Ons. |
| Python 3.12 | Only for the ML service (Part B). Download from python.org and tick "Add python.exe to PATH" when installing. |
| Internet | Only once, to install the Python libraries |
| Project folder | The whole project folder (not only one file), copied to a short path such as C:\DGA_Project. Not in OneDrive. Do not rename the numbered folders. |

# 3. Set up the computer (do this once)

- Copy the whole project folder to the computer, for example to C:\DGA_Project. You may leave out the folder 06_Python_ML\.venv, because it only works on the old computer.

- Install Python 3.12 (see Section 2).

- Open the folder C:\DGA_Project\06_Python_ML in Windows File Explorer and double-click Setup_Python_Environment.bat.

- A black window opens and installs the libraries. It takes a few minutes. Wait until it says "Finished" and press any key.

- Install MATLAB R2025b with Simulink, Simscape and Simscape Electrical.

If the black window shows red error text, send me a photo or copy of it.

# 4. Every time you start: prepare MATLAB

Do this each time you open MATLAB. It tells MATLAB where the project files are. The dashboard now also finds its own folders when it starts, so it no longer stops with the error "params_transformer is not found". This step is still recommended because the other files in this guide (scenarios and checks) use it.

- Start MATLAB R2025b.

- Look at the Current Folder panel on the left and the folder box at the top of the window. Click the small folder button next to the box, browse to C:\DGA_Project and select it. You should now see the numbered folders (04_MATLAB_Conventional, 05_Simulink_Model, and so on) in the Current Folder panel.

- In the Current Folder panel, find the file project_setup.m and double-click it. It opens in the Editor.

- Click the green Run button at the top of the Editor (Editor tab).

- If MATLAB asks "Change Folder or Add to Path", choose Change Folder.

- In the Command Window at the bottom you must see: Project paths added. Parameters loaded from params_transformer.m

If the dashboard still says "Project folder not found", the folder was changed or is incomplete: see Section 10.

# 5. Part A: run the Simulink simulation

- In the Current Folder panel, double-click the folder 05_Simulink_Model to open it.

- Double-click the file Transformer_Operating_Model.slx. The block diagram opens.

- Click the green Run button in the Simulink toolbar (Simulation tab). It takes about 10 seconds.

- To see the curves, open the Data Inspector (Simulation tab > Data Inspector) and tick the signals.

What you should see: the top-oil temperature rises slowly to about 78.6 Â°C and the hot-spot temperature to about 100.3 Â°C (rated load, 20 Â°C air).

The picture of the whole model is also saved as 05_Simulink_Model\figures\Figure_3_4_top_level.png, in case you want to show it without MATLAB.

## What to explain on the diagram

The model has eight blocks (subsystems). Point to them in this order:

| Block | What it does |
| --- | --- |
| SS1 | The 110 kV power grid (the source) |
| SS2 | The 40 MVA, 110/20 kV transformer |
| SS3 | Measures the current and the load factor |
| SS4 | The load, which changes with time |
| SS5 | Turns the electrical losses into heat |
| SS6 | The thermal network: oil and winding temperatures (IEC 60076-7 equations) |
| SS7 | Calculates the hot-spot temperature and the ageing rate |
| SS8 | Marks four sampling times (6, 12, 18 and 22 hours). It gives no gas values. |

Every block has a text note on it. All numbers come from one file, 05_Simulink_Model\params_transformer.m. To change a value (for example the air temperature), open that file, edit it, save, and run the model again.

# 6. Part C: run the dashboard (the app)

The dashboard has two helpers: MATLAB (already prepared in Section 4) and the ML service (Step 1 below). Do the steps in this order.

## Step 1: start the ML service

- Open C:\DGA_Project\09_API_FastAPI in Windows File Explorer.

- Double-click Start_ML_Service.bat. A black window opens.

- Wait until the window shows the line Uvicorn running on http://127.0.0.1:8000 (about 10 to 30 seconds).

- Leave this black window open during the whole demonstration. Do not close it.

- Optional check: open a web browser and go to http://127.0.0.1:8000/health. It should say the model is loaded. The page http://127.0.0.1:8000/docs lets you type five gas values and get a diagnosis.

## Step 2: open and run the dashboard

- Go back to MATLAB (prepared as in Section 4 is recommended, but the dashboard also finds its folders by itself).

- In the Current Folder panel, double-click the folder 10_Dashboard_Client.

- Double-click the file DGADashboard.mlapp. It opens in App Designer, which shows the app layout.

- In App Designer, click the green Run button at the top (Designer tab). The dashboard window opens.

- The status line at the bottom left says: Ready. Run the simulation or load a DGA file.

If the dashboard window is cut off on a small screen, make the window larger or move it up. It was designed for a window about 720 pixels high.

## Step 3: use the dashboard

The buttons are on the left side. There are two ways to use it.

Way 1: run the simulation and diagnose four records automatically (best for the lecturer)

- Click Run transformer simulation.

- The top graph draws the simulated top-oil temperature (blue) and hot-spot temperature (red) over 24 hours, with four dotted lines marked #1 to #4 (the sampling times).

- At each sampling time the dashboard takes the real DGA record that belongs to that event and diagnoses it. The table at the bottom fills with one row per event: time, record, ML diagnosis, how many of the 3 conventional methods agree, and the hot-spot temperature at that time.

Way 2: diagnose one record of your choice

- Click Load measured DGA file. A window opens in the folder 03_Data\processed. Select dga_master.csv and click Open.

- Under Record number (row) choose a number (type it or use the arrows).

- Click Diagnose selected record.

## How to read the dashboard

| Part of the screen | What it shows |
| --- | --- |
| Table of results (right, top) | The diagnosis of Rogers Ratio, IEC 60599, Duval Triangle and ML, and whether each agrees with ML |
| Probability table (right) | How sure the ML model is about each fault class |
| Duval Triangle picture (middle) | The measured sample plotted inside the Duval triangle |
| Gas table (left) | The five gas values (ppm) of the selected record |
| Agreement lamp (bottom right) | Green: all three conventional methods agree with ML. Amber: at least one does not agree. Grey: ML answer not available. |
| Text above the lamp (bottom right) | The ML model name, version and how long the answer took |

Fault classes: Normal, PD (partial discharge), D1 (low-energy discharge), D2 (high-energy discharge), T1, T2, T3 (thermal faults of rising temperature). The answers "ND" (not determined) and "DT" never count as agreement.

Tip for the lecturer: find one record where the lamp is green and one where it is amber, and explain why the methods differ.

The dashboard never invents a diagnosis, never creates or changes gas values, and never presents the simulated temperature as the cause of the measured gases.

## Step 4: finish

- Close the dashboard window.

- Close the black ML service window (or click in it and press Ctrl+C). This stops the service.

# 7. More files you can open and run

Each of these is a MATLAB file: in MATLAB, double-click it in the Current Folder panel, then click the green Run button. If MATLAB asks "Change Folder or Add to Path", choose Change Folder.

| File (inside the project folder) | What happens when you run it |
| --- | --- |
| 05_Simulink_Model\run_step36.m | Runs the three example scenarios (rated load, daily cycle, short overload). Pictures are saved in 11_Results\figures (files starting F4_19). Peak hot-spot: about 100.3, 99.9 and 129.0 Â°C. The load patterns are examples, not measured data. |
| 05_Simulink_Model\verify_step35.m | Compares the model with an independent calculation of the IEC 60076-7 equations. 15 checks should pass. |
| 05_Simulink_Model\verify_step37.m | Checks the sampling block SS8. 10 checks should pass. |
| 10_Dashboard_Client\verify_step40.m | Checks the link between the model and the dashboard (13 checks). Needs the ML service running. |
| 10_Dashboard_Client\run_testbench.m | Runs all 388 held-out records through the whole system. Needs the ML service running. Takes a few minutes. |

Numbers you can quote from the verification: largest difference after the first 10 minutes is 0.0014 K (top-oil) and 0.0129 K (hot-spot), against an accepted limit of 0.1 K. The test bench processed 388 records with 0 failed calls; the ML answers were identical to the offline results in all 388.

Saved evidence: 11_Results\tables\T4_10_simulink_verification.csv, 11_Results\figures\F4_18_simulink_verification.png and 10_Dashboard_Client\logs\testbench_log.csv.

# 8. A 10-minute talk plan

| Time | What to do |
| --- | --- |
| 1 min | Say what the project is for. Say that the simulation gives only the working conditions and creates no gas values. |
| 2 min | Open the Simulink model (Section 5). Walk through SS1 to SS8. |
| 1 min | Press Run. Show the top-oil temperature, hot-spot temperature and ageing. |
| 1 min | Show Figure 4.19 (file F4_19c_scenario_overload.png): in the overload scenario the hot-spot reaches about 129 Â°C. |
| 1 min | Show the verification result and the 0.1 K limit (Figure 4.18). |
| 3 min | Open the dashboard (Section 6). Click Run transformer simulation. Then diagnose one green and one amber record. |
| 1 min | State the limits (Section 9). |

If the computer fails, show the saved pictures instead:

- 11_Results\figures\F4_22_dashboard_annotated.png (the dashboard with notes)

- 05_Simulink_Model\figures\Figure_3_4_top_level.png (the whole model)

- 11_Results\figures\F4_18_simulink_verification.png and F4_19a, F4_19b, F4_19c (verification and scenarios)

# 9. Be honest about the limits

- The check of the Simulink model is verification (it matches the IEC equations). It is not validation against measurements from a real transformer.

- The thermal constants come from an open-source model, and the electrical data are typical values for a 40 MVA 110/20 kV unit, not from a real nameplate. The standard IEC 60076-7:2018 was not obtained, so these values are marked TO VERIFY.

- The three load scenarios and the four sampling times are examples, not measured data.

- The dashboard and the ML service are a local test bench on one computer, not a product on a network.

- Research result: ML was not shown to be better than the conventional methods on the main benchmark (IEC TC 10). It was partly better on the other two test sets. See Chapter 4 of the thesis.

# 10. Connect everything by hand on a new laptop

Everything in the project is joined by folder names, not by typed addresses. If you send the whole project folder to another laptop that has the same MATLAB version (R2025b), there are only five links to make. Do them in this order and test each one.

## Link 1: keep the folder layout

Copy the whole project folder and do not rename or move the numbered folders inside it. The dashboard and the model use these:

| Folder | Used for |
| --- | --- |
| 02_Standards | Duval triangle zones (drawn in the dashboard) |
| 03_Data\processed | dga_master.csv: the real DGA records the dashboard diagnoses |
| 04_MATLAB_Conventional | Rogers, IEC 60599 and Duval calculations |
| 05_Simulink_Model | The model and params_transformer.m (all model values) |
| 06_Python_ML | The released ML model (models folder), the Python code (src) and the Python environment (.venv) |
| 09_API_FastAPI | The ML service and Start_ML_Service.bat |
| 10_Dashboard_Client | The dashboard (DGADashboard.mlapp) and its helper files |

Put the folder on a short path such as C:\DGA_Project, not in OneDrive.

## Link 2: tell MATLAB where the folders are (MATLAB path)

The dashboard now does this by itself. If you want to do it by hand (or if it says "Project folder not found"), use one of these two ways:

Way 1 (easiest): open MATLAB, set the Current Folder to the project folder, double-click project_setup.m, click Run. The message "Project paths added" appears.

Way 2 (permanent, by clicking):

- In MATLAB click Home > Set Path.

- Click Add Folderâ€¦ and choose 04_MATLAB_Conventional. Repeat for 05_Simulink_Model and 10_Dashboard_Client (three folders; do not use "Add with Subfolders").

- Click Save, then Close. MATLAB now remembers the folders every time it starts.

If you move the project folder later, remove the old three folders in Set Path and add the new ones.

## Link 3: the Python environment

The Python environment is not copied to the new laptop (it only works where it was made). Install Python 3.12, then double-click 06_Python_ML\Setup_Python_Environment.bat and wait until it finishes (Section 3).

If you later move or rename the project folder, delete the folder 06_Python_ML\.venv and double-click Setup_Python_Environment.bat again.

## Link 4: the dashboard and the ML service

The dashboard calls the service at the address http://127.0.0.1:8000. The service listens at the same address. Both run on the same laptop, so nothing needs to be typed or changed. Start the service first (Start_ML_Service.bat), then the dashboard. If another program already uses port 8000, close that program.

## Link 5: the model and its values

The Simulink model reads its numbers from 05_Simulink_Model\params_transformer.m when it opens, and it looks for the real records in 03_Data\processed\dga_master.csv. Keep these two files where they are.

## Test every link by clicking

| Link | How to test | You should see |
| --- | --- | --- |
| 1 and 2 (folders, MATLAB path) | Double-click project_setup.m and click Run | "Project paths added" |
| 3 (Python environment) | Double-click Start_ML_Service.bat | "Uvicorn running on http://127.0.0.1:8000" |
| 4 (service) | In a web browser open http://127.0.0.1:8000/health | "model_loaded": true |
| 5 (model) | Open Transformer_Operating_Model.slx and click Run | Temperatures drawn, no error |
| All together | Open DGADashboard.mlapp, click Run, then "Run transformer simulation" | "4 of 4 sampling events diagnosed" |

# 11. If something goes wrong

| Problem | What to do |
| --- | --- |
| Dashboard says the ML is "NOT_CONNECTED" | The ML service is not running. Do Step 1 of Section 6 and wait for the line "Uvicorn running". Check that the black window is still open. |
| Dashboard says "Project folder not found" | The project folder is incomplete or was renamed. Check Link 1 and Link 2 in Section 10. |
| Error: params_transformer is not found (older version of the dashboard) | Use the new DGADashboard.mlapp, or run project_setup.m (Section 4) and start the dashboard again. |
| Black window closes at once, or says the Python environment is missing | Double-click 06_Python_ML\Setup_Python_Environment.bat (Section 3) and wait until it finishes. |
| "Port 8000 already in use" | The service is already running in another black window. Use that one, or close it and start again. |
| Simscape or Simscape Electrical not found | Install the add-on (Add-Ons > Get Add-Ons). |
| The model or app will not open | Your MATLAB is older than R2025b. |
| Strange cache errors in Simulink | Close the model. Delete the folder 05_Simulink_Model\slprj and the .slxc files. Restart MATLAB and do Section 4 again. |
| Numbers differ from this guide | Someone changed params_transformer.m. Copy the original back from your USB copy. |
| Any other error | Copy the exact error text and send it to me. |

# 12. Quick checklist

- Open MATLAB. Set the Current Folder to the project folder. Open and run project_setup.m.

- Double-click 09_API_FastAPI\Start_ML_Service.bat and leave the black window open.

- Double-click 05_Simulink_Model\Transformer_Operating_Model.slx and click Run.

- Double-click 10_Dashboard_Client\DGADashboard.mlapp, click Run in App Designer, then click Run transformer simulation.

- When finished, close the dashboard and the black window.

Test everything once on the presentation computer a day or two before the meeting.