Dashboard Update Report

Dashboard master control, freeze fix and explanation panel (update of Steps 39 and 40)

Environment: Claude Code (this chat), MATLAB through the MCP connection   |   Completed: 15 October 2026   |   Report version 1 (15 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The dashboard no longer freezes, and running it is enough. The freeze was reproduced and its cause found: the ML service had been started in a way that tied it to MATLAB's own output channel, and after about 60 requests the service stopped and MATLAB waited for it (request 62 waited 248.4 seconds). The service is now started detached from MATLAB; a stuck service is replaced automatically; the Simulink model is prepared behind a progress window at start-up; the buttons are switched off while a step runs; and the service is stopped when the dashboard is closed. A new panel, How to read this result, explains every result in plain words for the viewer. All 23 automatic checks pass, including the stress test that stopped the old version (400 of 400 requests answered, none failed) and the 19 + 13 checks of Steps 39 and 40.

# 1. Purpose of this update

The researcher reported that the software froze, and asked that the dashboard be the master control (running the app should be enough and everything should work), that the app show an explanation text so that a viewer can interpret each result, that every step be reported, and that the work not stop before everything works. This report describes how the cause was found, what was changed, what the explanation panel says and how it was checked.

# 2. Method used

## Approach

The dashboard froze, so the first step was to find the cause by measurement, not by guessing. The ML service was started again in the old way and called 400 times in a row from MATLAB while the time of every call was recorded. The service answered requests 1 to 61; request 62 waited 248.4 seconds and MATLAB did not react in that time. The cause is how the service was started: MATLAB's system() command gives the program it starts MATLAB's own output channel (a pipe with a small buffer of about 4 KB). The service writes one log line per request; after about 60 requests the buffer was full, nobody read it, the service stopped while writing the next line and MATLAB waited for the service.

Three more causes of a window that looks frozen were found and removed: a hung service still occupies the network port, so a new one could never start and the old code waited 90 seconds in vain; the first simulation in a MATLAB session compiles the Simulink model and took 54.4 seconds without any message; and nothing stopped a second click on a button while a step was still running.

The dashboard was then made the master control. It starts the service itself (detached from MATLAB, output to a log file), checks that the service answers before every diagnosis and restarts it when it does not, prepares the Simulink model behind a progress window at start-up, switches the buttons off while a step runs, offers a Restart ML service button, and stops the service when it is closed (only if it started it). A new text panel explains every result in plain words for the person who looks at the screen. Finally 23 automatic checks were written and run until all passed (verify_step43.m).

## Why this method

•  A fault of this kind cannot be repaired reliably by adding waits or timeouts: the measured wait of 248.4 s happened although a time limit of 10 s was set on the call. The cause had to be removed at its source (the shared output channel).

•  Starting a service through the Windows management service (WMI) gives the new program no handles of the caller; this is the standard way to start a background program that must outlive, and not depend on, the program that starts it.

•  A panel that explains each result serves a viewer who is not a DGA specialist: it names the fault types, says what the three classical methods and the ML model answered, how sure the model is, whether the methods agree and how far the answer should be trusted. The wording is fixed in one file (dashboard_explain.m) and only the numbers come from the program, so the text cannot contradict the screen.

•  Running every check again after each change until all pass (the loop) and re-running the 19 checks of Step 39 and the 13 checks of Step 40 shows that the repair did not break earlier results.

## Settings and rules

| Setting | Value |
| --- | --- |
| Service start | 09_API_FastAPI/launch_service_detached.ps1: WMI Win32_Process.Create, output to 09_API_FastAPI/logs/service.log, per-request access log off, log level warning |
| Health check | GET /health with a time limit of 2 s, before every diagnosis; failure leads to stop and restart (waits at most 60 s, reports every 0.5 s) |
| Start-up | service check/start, then one run of the Simulink model (warm-up, result not kept) |
| Window | 1350 x 690 pixels (the screen of the project laptop is 1366 x 768) |
| Reading aid in the text | 'clear majority' = ML class with more than half of the probability (a display rule, not a validated limit) |
| Checks | verify_step43.m: 23 checks; stress test 400 requests |
| Software | MATLAB 25.2.0.2998904 (R2025b), App Designer file written by the internal serializer; FastAPI service of Step 38 |

## Tools and programs

•  09_API_FastAPI/launch_service_detached.ps1, stop_service.ps1

•  10_Dashboard_Client/ensure_ml_service.m, stop_ml_service.m, dashboard_explain.m, verify_step43.m

•  10_Dashboard_Client/tools/DGADashboard_code.txt and build_dashboard_mlapp.m (write DGADashboard.mlapp)

•  00_Project_Admin/report_builder/update_register_step43u.ps1 (register, glossary, decision D42)

## Method references

[SW2] MATLAB R2025b, version 25.2.0.2998904, The MathWorks, Inc., Natick, MA, USA. https://www.mathworks.com/products/matlab.html

[SW6] FastAPI 0.143.0 (web framework), Uvicorn 0.54.0 (server), Pydantic 2.14.0 (input validation), HTTPX 0.28.1 (HTTP client for tests and the service check); Python packages pinned in 06_Python_ML/requirements.txt. https://fastapi.tiangolo.com/

# 3. Why the software froze (measured)

| What was measured | Result |
| --- | --- |
| State at the start of the session | A service process held port 8000 but did not answer: the health request timed out after 3 s |
| Reproduction with the old start method: requests answered | 1 to 61 |
| Request 62 | waited 248.4 s, until the service processes were stopped from outside; MATLAB itself did not respond meanwhile |
| First simulation of a fresh MATLAB session (whole run) | 54.4 s with no message (a repeated run: 12.4 s; the simulation alone: 3.3 s) |
| Same stress test after the fix | 400 requests in 27.6 s, 0 failed, median 64 ms, slowest 83 ms |

The full analysis, with the table of changed files, is in 10_Dashboard_Client/results/step43_freeze_analysis.md. In plain words: the old start gave the service MATLAB's output pipe; a pipe holds only about 4 KB; the service writes a line for every request; when the pipe was full, the service waited for someone to read it, and MATLAB waited for the service.

# 4. What was done, step by step

1.  Read the project memory (session summary, working preferences, plan) and the dashboard code. Found that the app waited up to 90 s in start-up with no message, and that the service could be started in a hidden window by system().

2.  Checked the running system: the service process was alive but did not answer. Stopped it and restarted it, then reproduced the freeze with a loop of 400 calls (result above).

3.  Wrote the repair: a start script that uses the Windows management service (09_API_FastAPI/launch_service_detached.ps1), a safe stop script, and a new ensure_ml_service.m that also replaces a stuck service. Repeated the 400-call test: all answered.

4.  Rebuilt the dashboard: health check before each diagnosis, busy lock on the buttons, progress windows, model warm-up at start, Restart ML service button, click on an event row, stop of the own service on close, and a fourth column with the explanation panel. The window was made 1350 x 690 pixels for the 1366 x 768 screen of the project laptop.

5.  Wrote dashboard_explain.m, the program that writes the explanation text, and checked its output on a screenshot of the app.

6.  Wrote verify_step43.m (23 checks) and ran it until every check passed (see Problems and fixes).

7.  Updated the how-to README (section 5), the dashboard README, the register (DF86-DF89), the glossary, the decision log (D42), CHANGELOG.md, SESSION_SUMMARY.md and the memory notes.

# 5. How the dashboard works now

| When | What the dashboard does by itself |
| --- | --- |
| It is started (DGADashboard) | Finds the project folders; loads params_transformer; checks the ML service and starts it detached if needed; runs the Simulink model once (warm-up); shows the welcome text. A window 'Starting the dashboard' shows each of these steps (about 25 s with a warm model, up to about 1 min on the first start). |
| Run transformer simulation | Switches the buttons off, shows a progress window, runs the model for 24 h, plots top-oil and hot-spot temperature, marks the sampling events, then diagnoses the record of each event and explains the run. |
| Diagnose selected record | Reads the five gases of the chosen row, computes Rogers, IEC 60599 and Duval in MATLAB, checks that the service answers (restarts it if not), asks the ML service, shows the tables, the Duval Triangle, the agreement lamp and the explanation. |
| A row of the event table is clicked | Shows that event's record, results and explanation again. |
| Restart ML service is pressed | Stops the service (also a stuck one) and starts it again. |
| The window is closed | Stops the ML service if this dashboard started it; leaves one that was started by hand. |

# 6. The explanation panel

The panel at the right edge is called How to read this result. At the start it explains what the dashboard does, what to press, which information comes from where (temperatures from the simulated transformer; gas values only from measured records) and what the fault types mean. After a diagnosis it explains that record; after a simulated day it first summarises the day (the sampling events and the simulation) and then the last record. Every number in it is taken from the program output; the fixed wording follows IEC 60599 (fault types, typical values) and the project decisions on agreement (D11, D25, D37).

| Part of the text | What it tells the viewer |
| --- | --- |
| Gas level | Whether every gas is at or below the IEC 60599 typical value (the classical methods then say Normal), with the warning that typical values are not fault limits |
| Classical methods | Rogers, IEC 60599 and Duval answers, each with the fault type in words; ND (no diagnosis), DT (mixed fault) and D1 or D2 are explained |
| Machine learning | Most probable class, its probability, the next two classes, whether one class has more than half of the probability, and a note when the model names a fault although all gases are within typical values |
| Agreement | What the lamp colour means and which method differs from the ML answer |
| How much to trust it | Decision support, not a verdict; on the IEC TC 10 cases of this study the ML model was not shown to be better than the classical methods; confirm with a repeat sample, the gas trend and an inspection |
| Simulation | Peak and final temperatures, load, the ageing rule (98 degC = rate 1, 6 K doubles it, TO VERIFY) and the loss of life of the run, with the reminder that the simulation is context and not the cause of the gases |

## Example of the text (record IECTC10_0002 and the simulated day)

The lines below were written by the program (results/step43_example_explanation.txt); nothing was edited.

WHAT THE DIAGNOSIS MEANS

Record IECTC10_0002

Measured gases (ppm): H2 37800, CH4 1740, C2H6 249, C2H4 8, C2H2 8. These values come from the data file as they are.

Gas level: at least one gas is above the typical value of IEC 60599 (Annex A), so the classical methods look at the gas ratios to name a fault type.

Classical methods:

- Rogers ratio: ND, no diagnosis: the ratios fall in no coded combination.

- IEC 60599 ratio: PD, partial discharges.

- Duval Triangle 1: PD, partial discharges.

Machine learning (Random Forest, model 1.0): most probable type PD (partial discharges), probability 81 %.

The next most probable types are D1 (12 %) and T1 (5 %).

The model has a clear majority for one type (more than half of the probability).

Agreement (amber lamp): 2 of the 3 classical methods agree with the ML answer. When methods disagree, the record is close to a boundary between fault types or is unusual: do not rely on one method alone.

Who differs from ML (PD): Rogers says ND. D1/D2 counts as agreeing with D1 or D2; DT and ND never count as agreeing.

HOW MUCH TO TRUST IT

This is decision support, not a verdict. On the inspection-confirmed IEC TC 10 cases used in this study, the ML model was not shown to be better than the classical methods (thesis, Chapter 4); use it as a second opinion. Confirm any fault indication with a repeat sample, the gas trend over time and, if needed, an inspection.

WHAT THE SIMULATION SHOWS

The transformer was simulated for 24 hours with an ambient temperature of 20 degC.

Top-oil temperature (blue): ends at 78.6 degC. Hot-spot temperature (red, the hottest point of the winding): peaks at 100.3 degC at 24.0 h and ends at 100.3 degC.

The load factor was constant at 0.98 times the rated load.

Insulation ageing: the paper insulation ages faster when the hot-spot is hotter. At a hot-spot of 98 degC the ageing rate is 1 (normal); every 6 K more doubles it (reference values of params_transformer.m, TO VERIFY against IEC 60076-7). Over this run the insulation aged as much as it would in 27.9 hours at the normal rate (loss of life).

The hot-spot was above 98 degC for part of the run, so the insulation aged faster than the normal rate during that time.

Remember: this is a thermal model of the operating condition. It gives context for the gas results; it does not prove or disprove a fault.

Figure  The dashboard after a simulated day and a click on sampling event 2 (program screenshot)

# 7. Checks

| Check (verify_step43.m) | Result |
| --- | --- |
| A1 the service starts from MATLAB without blocking MATLAB (detached start) | PASS |
| A2 400 requests in a row through that service: none fails (the old start froze at request 62) | PASS |
| A3 the service writes to its own log file, not to a pipe of MATLAB (log exists, no request lines) | PASS |
| B a service that holds the port but does not answer is stopped and replaced by a working one | PASS |
| C1 cold start with the service stopped: the app starts the service and reports Ready | PASS |
| C2 the explanation panel shows the welcome text (how to use, two kinds of information, fault types) | PASS |
| C3 all buttons are enabled after the start | PASS |
| D1 the run completes (simulation + 4 sampling events) without error | PASS |
| D2 the simulation explanation quotes the program values (peak hot-spot, final top-oil, loss of life) | PASS |
| D3 after a run the summary of the events comes first, then the simulation, then the last record | PASS |
| D4 the explanation names the record that is shown and its three conventional answers and the ML class | PASS |
| D5 all buttons are enabled after the run | PASS |
| E clicking event 2 shows its record (spinner, tables, explanation first) | PASS |
| G0 (set-up) the service is stopped | PASS |
| G the service was stopped before the run: the app restarts it and all 4 events are diagnosed by ML | PASS |
| I1 buttons enabled again after that run | PASS |
| F the explanation of every held-out record is built without error, has no NaN, names Rogers, IEC, Duval and the ML class, and the agreement text matches the lamp | PASS |
| F2 with the ML service not connected the explanation says so and keeps the classical results | PASS |
| H1 closing the window stops the service that this app started | PASS |
| H2 closing the window leaves a service that this app did not start | PASS |
| I2 a failed diagnosis (file missing) gives a message and the buttons are enabled again | PASS |
| J1 the 19 checks of verify_step39 still pass | PASS |
| J2 the 13 checks of verify_step40 still pass | PASS |

Check F built the explanation of all 388 held-out records (248 of them with amber agreement) without error and without any NaN in the text, named the three classical answers and the ML class in each, and checked that the agreement text matches the lamp colour.

# 8. Problems and fixes

•  The first full run of the checks stopped at check C3 because the test helper put buttons of different types into one array (a fault in the test, not in the app); corrected.

•  The second run failed at check D because the test read a private property of the app (SimResult); the property was made public so that the check can compare the plotted values with the program values.

•  Check B (a stuck service is replaced) failed twice at its set-up, not in the app: the stuck-service stand-in could not be created, first because the default execution policy of PowerShell blocks script files, then because the MATLAB temp folder name contains a space. The stand-in was first created by hand and the real recovery code was run against it (the stuck service was stopped and replaced in about 15 s); the test was then corrected and the whole verification repeated.

•  One earlier idea was not used: a longer or shorter time limit on the call. The measured wait (248.4 s) happened with a 10 s limit set, so a limit does not protect against this fault; the health check before each call and the detached start do.

•  The old ensure_ml_service.m and stop_ml_service.m were overwritten before the backup copy was made; the backup folder tools/backup_before_masterctl therefore holds the new versions of these two files (the old version is described in the freeze analysis). The old app and its code are in the backup.

# 9. Decisions

•  D42 (proposed): the cause and the repair of the freeze; the start of the service detached from MATLAB; the health check before each diagnosis; the busy lock, progress windows and warm-up; the Restart button; stop on close only for a service that the app started; the explanation panel and its rules; the checks. The reading aid 'more than half of the probability = clear majority' is a display rule.

# 10. Files produced

•  09_API_FastAPI/launch_service_detached.ps1, stop_service.ps1 (new); logs/service.log (written when the service runs)

•  10_Dashboard_Client/DGADashboard.mlapp (rebuilt), dashboard_explain.m (new), ensure_ml_service.m, stop_ml_service.m (rewritten), verify_step43.m (new), tools/DGADashboard_code.txt and build_dashboard_mlapp.m (updated), tools/backup_before_masterctl/ (previous app and code)

•  10_Dashboard_Client/results/step43_checks.csv, step43_freeze_analysis.md, step43_example_explanation.txt, step43_dashboard_screenshot.png; code_manifest_masterctl_2026-10-15.sha256

# 11. What was achieved

•  The cause of the freeze was found by reproduction and removed: the service is started detached from MATLAB. The same stress test that stopped the old start at request 62 now passes: 400 of 400 requests answered, none failed, median 64 ms.

•  A service that is stuck (holds the port, does not answer) is detected, stopped and replaced by a working one in 14 s.

•  The dashboard is the master control: running DGADashboard is enough (it starts the service, prepares the model, restarts the service when needed and stops it on close).

•  A new panel explains each result in plain words (simulation, the three classical methods, the ML class and probability, agreement, fault types, how much to trust it); its text was built without error for all 388 held-out records.

•  All 23 checks pass, including the 19 checks of Step 39 and the 13 checks of Step 40.

# 12. Record of this step

| Item | Record |
| --- | --- |
| Step | Update of Steps 39-40: dashboard freeze fix, master control and explanation panel (decision D42) |
| Environment | Claude Code (this chat) through the MATLAB MCP connection |
| Completed | 15 October 2026 |
| Status | Done (D42 proposed, to be confirmed by the researcher) |
| Main inputs | DGADashboard.mlapp of Steps 39-40; the FastAPI service of Step 38; the model of Step 33; dga_master.csv |
| Main outputs | DGADashboard.mlapp (rebuilt), dashboard_explain.m, ensure_ml_service.m, stop_ml_service.m, launch_service_detached.ps1, stop_service.ps1, verify_step43.m, results/step43_checks.csv, step43_freeze_analysis.md, step43_dashboard_screenshot.png |
| Checks | verify_step43.m: 23 of 23 PASS |
| Decisions | D42 |

# 13. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DF86 | verify_step43.m: 23 checks (400-request stress test through the detached service start, recovery from a hung service, cold start of the app, run + explanation text, click on an event, explanation text of all 388 held-out records, service stopped during use, closing the window, buttons after a failure, regression of the 19 + 13 older checks). Use: Evidence that the dashboard is the master control and no longer freezes. | File: 10_Dashboard_Client/results/step43_checks.csv; SHA-256 F04854F8773A7636... |
| DF87 | step43_freeze_analysis.md: observation, reproduction (request 62 waited 248.4 s), cause (service started with system() inherited MATLAB's 4 KB output pipe), fix, second cause (cold first run 54.4 s), result after the fix. Use: Record of why the software froze and what was changed. | File: 10_Dashboard_Client/results/step43_freeze_analysis.md; SHA-256 27D97DA0000DD8F3... |
| DF88 | step43_dashboard_screenshot.png: the app after a simulated day and a click on sampling event 2 (exportapp). Use: Candidate replacement of Figure 4.22 (not yet used in the thesis). | File: 10_Dashboard_Client/results/step43_dashboard_screenshot.png; SHA-256 60BD364E3113FABD... |
| DF89 | DGADashboard.mlapp, tools/DGADashboard_code.txt, tools/build_dashboard_mlapp.m, dashboard_explain.m, ensure_ml_service.m, stop_ml_service.m, verify_step43.m, 09_API_FastAPI/launch_service_detached.ps1, stop_service.ps1. Previous app and code: tools/backup_before_masterctl/. Use: Fingerprints of the master-control code. | File: 10_Dashboard_Client/code_manifest_masterctl_2026-10-15.sha256; SHA-256 558BBDCD768E9C4D... |
| DF71 | step39_checks.csv (19 checks of verify_step39.m), step39_three_records.csv (the three known records), step39_held_out_comparison.csv (388 held-out records: app answers against offline results). Use: Evidence for the Step 39 check: known records give the offline answers. | File: 10_Dashboard_Client/results/step39_checks.csv; SHA-256 2DA3E3899E47A1C5... |
| DF74 | step40_checks.csv (13 checks of verify_step40.m) and step40_event_run.csv (the four sampling events of the full simulated day as the dashboard shows them: time, record_id, ML class, conventional methods agreeing, simulated hot-spot temperature). Use: Evidence for the Step 40 check: a full simulated day runs from the app. | File: 10_Dashboard_Client/results/step40_checks.csv; SHA-256 9CA8E7417EB4A616... |
| SW2 | MATLAB R2025b, version 25.2.0.2998904, The MathWorks, Inc., Natick, MA, USA. Use: Runs the conventional-method functions, unit tests, batch run and Duval figures (Steps 14-17). | https://www.mathworks.com/products/matlab.html |
| SW6 | FastAPI 0.143.0 (web framework), Uvicorn 0.54.0 (server), Pydantic 2.14.0 (input validation), HTTPX 0.28.1 (HTTP client for tests and the service check); Python packages pinned in 06_Python_ML/requirements.txt. Use: Runs the diagnosis service of Step 38 and its tests. | https://fastapi.tiangolo.com/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 14. How this helps the next steps

Next step: Step 43 (thesis writing, already drafted as 12_Thesis/Thesis_Draft_v2.docx): replace the dashboard figure by the new screenshot and describe the master control and the explanation panel in the dashboard section; the supervisor demonstration can start from the single command DGADashboard.

•  Step 43 (the thesis) can describe the dashboard as a self-starting master control and show the new screenshot (results/step43_dashboard_screenshot.png) instead of the earlier Figure 4.22.

•  The demonstration for the supervisor needs one command (DGADashboard); the how-to README (section 5) was rewritten accordingly.

•  The explanation text gives the viewer the interpretation that the thesis Chapter 4 gives in writing.

# 15. Open items and limitations

•  Figure 4.22 of the thesis and the Step 39 and 40 reports still show the layout before this update; the new screenshot is a candidate replacement (not yet used).

•  Not tested on a second computer. The explanation text assumes the project folders as delivered.

•  The statement in the panel that the ML model was not shown to be better than the classical methods on IEC TC 10 repeats the final verdict of Step 31; it must be kept in line with the thesis.

•  The reference values for the ageing text (98 degC and 6 K) are those of params_transformer.m and are still marked TO VERIFY against IEC 60076-7.

•  The service is stopped on close only when the dashboard started it; a service started by hand stays running.

•  dashboard_explain.m: the number format of the gas values was changed after the last full run of verify_step43 (checked on one record).

•  The full verification takes about 20 minutes because it also repeats the 388-record checks of Steps 39 and 40.

# 16. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| D2 | discharges of high energy | Arcing with power follow-through: extensive carbonisation, metal fusion, sometimes tripping of the equipment. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| DT | mixture of thermal and electrical faults | A zone of the Duval Triangle 1 for cases that look partly thermal and partly electrical. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| Duval Triangle 1 | graphical DGA method by M. Duval | The shares of CH4, C2H4 and C2H2 are plotted as one point in a triangle divided into fault zones. |
| Rogers ratios | older gas-ratio method by R.R. Rogers | A ratio table that names faults from three gas ratios; kept in IEEE C57.104. |
| Typical values | 90 % typical gas concentrations | Levels below which about 90 % of transformers in service are found; not limit values. |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Median, quartiles | middle value and the values a quarter and three quarters of the way up | Describe typical gas levels without being pulled by extreme values. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| Simulink, Simscape | MATLAB's block-diagram modelling tool and its physical-modelling library | Used to model the transformer's operating conditions (Simulink Agentic Toolkit); it never makes gas values. |
| D1-D42 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| ND (no diagnosis) | No diagnosis | The answer of a method when no rule applies or a ratio it needs cannot be calculated. It is a result and is never deleted. |
| Unit test (matlab.unittest) | Automatic test of one small piece of code | A test that feeds a function a known input and checks the answer, so that any later change that breaks the function is noticed at once. |
| Majority baseline | reference model | Always predicts the most common class; any useful model must do clearly better. |
| Gas-level importance | shuffling one gas and everything made from it | One raw gas is shuffled before the features are built, so all its ratios and percentages move together; this avoids under-rating gases whose information is shared by several features. |
| NaN (not measured) | Not a Number, used here for a gas that was not measured | A marker for a missing value. It is different from 0 ppm: 0 ppm means the gas was measured and not found, NaN means nobody measured it, so no ratio or percentage can be calculated from it. |
| Simulink | MathWorks block-diagram simulation environment | Software in which the model is drawn as blocks and lines and simulated over time. |
| Top-oil temperature | Temperature of the oil at the top of the tank | The oil temperature used in the thermal model; it rises with load and falls back towards ambient. |
| Hot-spot temperature | Temperature of the hottest part of the winding | The winding temperature that mostly decides how fast the paper insulation ages; it is the top-oil temperature plus a load-dependent rise. |
| Relative ageing rate V | How many times faster than normal the paper ages | V = 1 at the reference hot-spot temperature (98 degC); every 6 K more doubles it. The loss of life is the sum of V over time. |
| IEC 60076-7 | IEC loading guide for oil-immersed power transformers | The standard that gives the equations for oil and hot-spot temperature and for ageing under a changing load. |
| Loss of life (L) | Equivalent hours of insulation ageing at the reference hot-spot temperature | The sum of the ageing rate over time: L = 24 h would mean the insulation aged as much as in 24 hours at 98 degC. |
| Sampling event | A moment in simulated time at which a gas sample would be taken | The model only says when; the gas values come from the real measured record in the data file, never from the model. |
| Held-out record | A record of the master table that is not used for development | A record kept aside (benchmark, internal test or external test) so that the methods are judged on data they did not learn from. |
| Agreement flag | Lamp that says whether the conventional methods agree with the ML diagnosis | Green: all three conventional methods give the same class as ML. Amber: at least one does not. Grey: no ML answer. |
| App Designer | MATLAB tool for building apps (.mlapp files) | The program in which DGADashboard.mlapp is edited; the file can also be run without opening it. |
| Event table | List of the sampling events of a simulated run in the dashboard | One row per sampling event: time, record, ML class, how many conventional methods agree, and the simulated hot-spot temperature at that time. |
| Warm-up call | One of the first calls to the service, which can be slower than the later ones | The first few requests set up the connection; they are flagged in the log so that they can be excluded or kept openly. |
| HTTP | Hypertext Transfer Protocol | The message format of the web; the dashboard sends a request and the service sends back an answer with a status code (200 = OK, 422 = input refused). |
| FastAPI | Python framework for web services | The library used to build the diagnosis service; it also checks every input against the declared rules. |
| Endpoint | one address of a web service | For example POST /diagnose (send a sample, get a diagnosis) or GET /health (is the service alive?). |
| Master control | one program that starts and supervises the others | The dashboard starts the ML service, prepares the Simulink model, checks that the service answers before each diagnosis, and stops the service when the dashboard is closed. |
| Detached start | starting a program so that it shares no connection with the program that started it | The ML service is started in a way that leaves MATLAB's own output channel unused; if they were shared, a full channel could stop the service and freeze MATLAB. |
| Access log | a line written by a web service for every request it answers | It was the lines of this log that filled a small buffer and stopped the service in the old start method. |