Dashboard Update Report

Dashboard redesign: verdict, scenarios, sample sets and record picker (update of Steps 39, 40 and 43)

Environment: Claude Code (this chat), MATLAB through the MCP connection   |   Completed: 17 October 2026   |   Report version 1 (17 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The dashboard now answers first and explains second. A coloured banner says whether the sample is healthy (green), has a fault of a named type (red), or needs a closer look (amber); four cards show the answers of Rogers, IEC 60599, Duval and the ML model with the word AGREES or DIFFERS; a table lists every sample of a run with all four answers and the verdict; and a tab shows the standard procedure step by step with the numbers of the sample. The demonstration is no longer the same four PD records: three operating conditions and three sample sets can be chosen, and the mixed set shows a healthy sample and every fault type in one run. A record picker chooses a record of a given fault type. All 18 new checks pass, the older checks of Steps 39, 40 and 43 pass (23 of 23), and on the 388 held-out records the verdict called 242 of 346 known faults a fault, with the exact type right in 217 of 242 cases.

# 1. Purpose of this update

The researcher reported that the app showed only numbers that could not be used: the comparison between Rogers, IEC 60599, Duval and ML was not visible, the fault and the healthy state were not visible, and there was no interpretation. The researcher asked for both varied demonstration records and a record picker, for a step-by-step layout that follows the internationally approved procedure, and for the whole project to be explained in simple terms. This report describes the cause, the redesign and its checks; the plain-language explanation is the document Project_Explained_Simply.docx.

# 2. Method used

## Approach

The researcher looked at the dashboard and said that it showed only numbers: the comparison between the methods was not visible, neither the fault state nor the healthy state was visible, there was no interpretation, and the output was always the same. The cause was measured first, from the saved test-bench log of Step 41: the first version always ran the constant rated-load scenario and always took the first four held-out records, and all four are true PD records, so the ML answer was PD every time; the thesis test bench, in contrast, ran all 388 records and produced all seven classes.

The screen was then redesigned so that the answer comes first and the evidence second, in the order of the international procedure (IEC 60599 and IEEE Std C57.104-2008): compare each gas with its typical value; if all five gases are at or below the typical values the transformer is healthy; otherwise read the fault type with the three classical methods and the ML model, compare them, and give one verdict with a recommended action. The verdict rule is a vote: each of the four methods gives one vote, the IEC dual answer D1/D2 votes for both D1 and D2, DT and ND give no vote, and the class with the most votes is the verdict when it has at least two votes and no tie; otherwise the banner says CHECK.

Variety was added in two ways, as the researcher asked for both: a choice of operating condition (three scenarios of Step 36) and of sample set (a mixed set with a healthy sample and one record of each fault type, a random set, and the first four records), and a record picker with a fault-type list. The sampling times and the stop time are passed to the unchanged Simulink model as values of the run; the record that belongs to each sampling event is looked up outside the model, so the model still holds no gas value.

Last, the new logic was tested on its own (10 tests, all 388 held-out records), the whole app was tested through its buttons (18 checks), and the older checks of Steps 39, 40 and 43 were run again. The first run of verify_step43 after the redesign found two changes of behaviour of the Step 40 run (see Problems and fixes); they were repaired and the full verification was repeated.

## Why this method

•  A viewer needs the conclusion before the numbers. Putting the verdict in a coloured banner, the four answers on four cards with one word each (AGREES, DIFFERS), and a table with one row per sample makes the comparison of the methods visible at a glance.

•  A vote is a simple rule that can be explained in one sentence and that uses no new threshold. It was chosen over a trained combination of the four answers because that would be a new classifier that would need its own validation. The rule is stated as a display rule, not a result of the study.

•  The healthy state is exactly the normality gate that the study already used (decision D11, typical values of IEC 60599 Annex A). The screen therefore does not contradict the thesis tables. The gate lets some faults with very low gas levels pass as healthy; the report and the thesis say so.

•  Choosing the sample from a fixed seed that grows after each press gives variety and still lets a result be reproduced. The 'first four' set is kept so that the checks of Steps 40 and 43 still apply unchanged.

## Settings and rules

| Setting | Value |
| --- | --- |
| Scenarios | scenarios.m of Step 36 (constant rated load 24 h; daily cycle 3 days with the last day shown; short overload 24 h) |
| Sampling times | 4 samples: 6, 12, 18, 22 h; other numbers n: n equal steps of 24/(n+1) h (7 samples: 3, 6, ... 21 h); inside the shown 24 h |
| Mixed set | one held-out record (data_role not development) of each known class Normal, PD, D1, D2, T1, T2, T3; random pick with seed 1, 2, 3 ... (seed + 1 after each press) |
| Verdict rule | one vote per method; D1/D2 votes for D1 and D2; DT, ND and a missing ML answer give no vote; at least 2 votes and no tie, otherwise CHECK |
| Typical values | IEC 60599:1999/AMD1:2007 Table A.2, read from 02_Standards/iec_typical_values.csv through load_standards (no number typed in the new code) |
| Window | 1380 x 740 pixels |
| Checks | verify_step44.m: 18 checks; test_dashboard_verdict.m: 10 tests; verify_step43.m: 23 checks (includes verify_step39 and verify_step40) |
| Software | MATLAB 25.2.0.2998904 (R2025b); App Designer file written by the internal serializer from tools/dashboard_components.m and tools/DGADashboard_code.txt |

## Tools and programs

•  10_Dashboard_Client/dashboard_verdict.m, dashboard_samples.m, sim_window.m, dashboard_explain.m, test_dashboard_verdict.m, verify_step44.m

•  10_Dashboard_Client/tools/dashboard_components.m, DGADashboard_code.txt, build_dashboard_mlapp.m, make_figure_4_22.m

•  05_Simulink_Model/run_transformer_simulation.m (optional second argument opts)

## Method references

[SW2] MATLAB R2025b, version 25.2.0.2998904, The MathWorks, Inc., Natick, MA, USA. https://www.mathworks.com/products/matlab.html

[SW6] FastAPI 0.143.0 (web framework), Uvicorn 0.54.0 (server), Pydantic 2.14.0 (input validation), HTTPX 0.28.1 (HTTP client for tests and the service check); Python packages pinned in 06_Python_ML/requirements.txt. https://fastapi.tiangolo.com/

# 3. Why the output was always the same (measured)

| What was found | Result |
| --- | --- |
| Scenario of every run of the first version | constant rated load, 24 h |
| Records of every run | IECTC10_0001 to IECTC10_0004 (the first four held-out records); all four have the true class PD |
| ML answer at these records | PD every time |
| Rogers answer at these records | ND (no diagnosis) at all four |
| The thesis test bench (Step 41) | ran all 388 held-out records; every one of the seven classes appears among the ML answers |

# 4. What was done, step by step

1.  Measured why the output was static (table above) and checked that the model can take more than four sampling times and other load profiles as run values: seven sampling times worked with the unchanged model.

2.  Backed up the app, the explanation text and the checks to 10_Dashboard_Client/tools/backup_before_redesign/.

3.  Wrote the verdict logic (dashboard_verdict.m), the sample chooser (dashboard_samples.m) and the window helper for the daily cycle (sim_window.m), and tested them on all 388 held-out records without the ML service (test_dashboard_verdict.m: 10 of 10).

4.  Extended run_transformer_simulation.m with optional run values (stop time, sampling times) and wrote the new component list and callbacks; rebuilt DGADashboard.mlapp (75 components).

5.  Wrote verify_step44.m and ran it; fixed the layout after looking at the screens (the sample table cut off rows; a label overlapped a bar).

6.  Ran the older checks again (verify_step43 including 39 and 40), repaired two changes of behaviour, and repeated the full verification.

7.  Regenerated the annotated screenshot (Figure 8.6), rewrote the dashboard section of thesis Chapter 8 (Thesis_Draft_v3.docx), updated the how-to README, the dashboard README, the register (DF90-DF93), decision D43, CHANGELOG.md and SESSION_SUMMARY.md.

# 5. The new screen

Figure  The redesigned dashboard after a simulated day with seven oil samples (program screenshot with numbered parts)

| Part | What it shows |
| --- | --- |
| 1 and 2 (left) | Operating condition (rated, daily cycle, overload) and the sample set (mixed, random, first four) |
| 3 and 4 (left) | Run simulation + diagnose; pick a random record of a chosen fault type |
| 5 Banner | HEALTHY (green), FAULT with type (red), WATCH or CHECK (amber); the reason; what to do |
| 6 and 7 Cards | Rogers, IEC 60599, Duval, ML: answer, meaning, AGREES / DIFFERS / NO ANSWER; known label of the record |
| 8 Sample table | One row per sample: known label, four answers, agreement count, verdict, hot-spot temperature |
| 9, 10, 11 Charts | Gas against typical value (log scale), Duval Triangle with the sample, ML probabilities |
| 12 Tabs | Charts; Step by step; Explanation in words; Tables; Simulation (operating condition) |

# 6. How the verdict is made

| Situation | Banner |
| --- | --- |
| All five gases at or below the IEC 60599 typical values and ML does not name a fault | HEALTHY (green) |
| All five gases at or below the typical values, but the ML model names a fault | WATCH (amber) |
| At least one gas above typical and one class has at least two votes (and no tie): a fault class | FAULT with the type (red); strong if all voting methods agree, majority if more than half |
| At least one gas above typical but the methods agree on Normal | WATCH (amber) |
| At least one gas above typical and no class has two votes | CHECK (amber) |

Votes: Rogers, IEC 60599, Duval and ML give one vote each. D1/D2 (IEC) votes for D1 and for D2. DT (Duval), ND (no diagnosis) and a missing ML answer give no vote. If the ML service is not reachable the verdict is made from the three classical methods (three voters).

# 7. How well the verdict agrees with the known classes (descriptive)

The verdict was computed for all 388 held-out records using the ML answers saved by the test bench (a descriptive check; it is not a new statistical test and the verdict rule is not a validated classifier).

| Question | Result |
| --- | --- |
| Records with a known fault | 346 |
| Verdict FAULT | 242 |
| Verdict HEALTHY (faults with very low gas levels that pass the typical-value check) | 7 |
| Verdict WATCH or CHECK | 97 |
| Known normal records called HEALTHY | 7 of 10 |
| Fault verdicts with a known class: exact type right | 217 of 242 |
| Fault verdicts with a known class: right family (electrical or thermal) | 240 of 242 |

# 8. Checks

| Check (verify_step44.m) | Result |
| --- | --- |
| start screen: banner says it is waiting, cards are empty, the welcome text names the colours | PASS |
| mixed run: 7 sampling events, no error, all diagnosed | PASS |
| mixed run: the 7 records are the healthy sample and one of each fault type, in the order Normal PD D1 D2 T1 T2 T3 | PASS |
| mixed run: sampling times 3, 6, ... 21 h (7 samples spread over the 24 h) | PASS |
| mixed run: the table shows both states - at least one HEALTHY or WATCH and at least one FAULT | PASS |
| event table: columns Rogers, IEC 60599, Duval, ML and Verdict are filled for every sample (the comparison of the methods in one table) | PASS |
| clicking each of the 7 samples shows its verdict banner (text, colour), the four method cards, the gas and probability charts and the step-by-step text | PASS |
| banner colour: green for healthy, red for fault | PASS |
| the diagnoses on the cards equal a fresh run of conventional_diagnosis on the file values | PASS |
| gas values used in the 7 diagnoses are those of the file (nothing comes from the model) | PASS |
| a second press with "Mixed" gives a different set of 7 (new seed), again one of each class | PASS |
| record picker: for each type (Normal, PD, D1, D2, T1, T2, T3) a record of that known class is chosen and diagnosed | PASS |
| record picker: "Any record" works | PASS |
| Diagnose selected record still works for record number 5 | PASS |
| ML not reachable: no error, ML card says n/a, verdict from the 3 classical methods (3 voters) | PASS |
| scenario "Short overload": 4 events at 6, 12, 18, 22 h; the hot-spot rises during the overload (peak above the rated-load run) | PASS |
| scenario "Daily load cycle": 72 h simulated, the last 24 h shown, 7 events inside the shown day, all diagnosed | PASS |
| step-by-step text has the 8 steps and a verdict, no NaN/Inf | PASS |

In addition: test_dashboard_verdict.m (10 of 10), verify_step43.m (23 of 23, which includes verify_step39 with 19 and verify_step40 with 13 checks), Python tests 154 passed, MATLAB tests 93 passed, and the Simulink checks of Steps 33, 35 and 37 (9, 15 and 10 checks) pass again on the unchanged model (file checksum identical to the one recorded on 13 October 2026).

# 9. Problems and fixes

•  The first run of verify_step44 had 16 of 18 passes. Both failures were in the test, not in the app: the test required the daily-cycle window to start at exactly 0 h (the first stored point after 48 h is at 0.003 h), and compared the overload event times exactly (they are 6.0000000001 h). The tolerances were set.

•  The first run of verify_step43 after the redesign passed 22 of 23: verify_step40 passed only 11 of 13. The new run code (1) set the default DGA file before the status message was written, so the message 'using dga_master.csv' disappeared, and (2) built the sample list from the loaded file, so a file with one record gave 1 of 1 events instead of '1 of 4' with the other records reported as missing. Both behaviours of Step 40 were restored in the app (the first-four set is looked up by record_id from the project list), and the verification repeated: 23 of 23.

•  In the first screenshots the sample table showed only four of the seven rows, a label overlapped a bar of the gas chart and the numbering discs covered text in Figure 8.6. Row heights and label positions were changed and the figure was regenerated.

# 10. Decisions

•  D43 (proposed): the verdict banner and its colours; the vote rule; the healthy state equal to the IEC 60599 typical-value gate of D11; the cards and the use of the known label for the right/wrong note only; scenario and sample-set choices; the seed rule; the sampling times; the descriptive check on the 388 records.

# 11. Files produced

•  10_Dashboard_Client/DGADashboard.mlapp (rebuilt), dashboard_verdict.m, dashboard_samples.m, sim_window.m, dashboard_explain.m (steps and label added), test_dashboard_verdict.m, verify_step44.m, tools/dashboard_components.m, DGADashboard_code.txt, build_dashboard_mlapp.m, make_figure_4_22.m, tools/backup_before_redesign/

•  05_Simulink_Model/run_transformer_simulation.m (optional second argument)

•  10_Dashboard_Client/results/step44_checks.csv, step44_mixed_run.csv, step44_screen*.png, dashboard_verdict_summary.csv, dashboard_verdict_check.csv, dashboard_verdict_tests.csv; code_manifest_redesign_2026-10-17.sha256

•  11_Results/figures/F4_22_dashboard_annotated.png (Figure 8.6 of the thesis), 12_Thesis/Thesis_Draft_v3.docx, 00_Project_Admin/Project_Explained_Simply.docx

# 12. What was achieved

•  The screen now gives the answer first: a green HEALTHY, red FAULT (with the type) or amber WATCH / CHECK banner with the reason and the recommended action, and four method cards that say AGREES or DIFFERS.

•  The sample table shows, for every sample of a run, the known label, the answers of Rogers, IEC 60599, Duval and ML, the number of agreeing classical methods and the verdict: the comparison of the methods is visible.

•  Variety: three operating conditions, three sample sets (the mixed set shows a healthy sample and every fault type in one run) and a record picker by fault type. A second press of the mixed set gives a different set.

•  The tab 'Step by step' follows the order of IEC 60599 / IEEE C57.104 with the numbers of the sample; the tab 'Explanation in words' keeps the plain-language text.

•  All 18 checks of verify_step44 pass; verify_step43 passes 23 of 23 (including the 19 checks of Step 39 and the 13 of Step 40); the 10 tests of the verdict logic pass; Python 154 tests and MATLAB 93 tests pass.

•  Descriptive result on the 388 held-out records: of 346 records with a known fault the verdict was FAULT for 242, HEALTHY for 7 and WATCH or CHECK for 97; when the verdict was FAULT the exact type was right for 217 of 242 and the right family for 240.

# 13. Record of this step

| Item | Record |
| --- | --- |
| Step | Update of Steps 39, 40 and 43: dashboard redesign (decision D43) |
| Environment | Claude Code (this chat) through the MATLAB MCP connection and batch MATLAB |
| Completed | 17 October 2026 |
| Status | Done (D43 proposed, to be confirmed by the researcher) |
| Main inputs | DGADashboard.mlapp of D42; scenarios.m; dga_master.csv; testbench_log.csv; the FastAPI service of Step 38 |
| Main outputs | DGADashboard.mlapp (rebuilt), dashboard_verdict.m, dashboard_samples.m, sim_window.m, dashboard_explain.m, verify_step44.m, test_dashboard_verdict.m, results/step44_*.csv and screens, results/dashboard_verdict_*.csv, Figure 8.6 of the thesis |
| Checks | verify_step44.m: 18 of 18 PASS; verify_step43.m: 23 of 23 PASS |
| Decisions | D43 |

# 14. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DF90 | DGADashboard.mlapp, dashboard_verdict.m, dashboard_samples.m, sim_window.m, dashboard_explain.m, tests, builders, run_transformer_simulation.m (opts). Previous app and code: tools/backup_before_redesign/. Use: Fingerprints of the redesigned dashboard code (D43). | File: 10_Dashboard_Client/code_manifest_redesign_2026-10-17.sha256; SHA-256 422C32D54CB0F763... |
| DF91 | step44_checks.csv (18 checks), step44_mixed_run.csv, step44_screen*.png (screens of the start, a healthy sample, a fault, overload and daily scenarios). Use: Evidence that scenarios, sample sets, picker, verdict and cards work (D43). | File: 10_Dashboard_Client/results/step44_checks.csv; SHA-256 121600427F254749... |
| DF92 | dashboard_verdict_summary.csv, dashboard_verdict_check.csv, dashboard_verdict_tests.csv (test_dashboard_verdict.m): descriptive, uses the ML answers saved in testbench_log.csv. Use: Numbers of thesis Chapter 8 (how often the verdict is right). | File: 10_Dashboard_Client/results/dashboard_verdict_summary.csv; SHA-256 9FEED1D0A0CC0BA8... |
| DF71 | step39_checks.csv (19 checks of verify_step39.m), step39_three_records.csv (the three known records), step39_held_out_comparison.csv (388 held-out records: app answers against offline results). Use: Evidence for the Step 39 check: known records give the offline answers. | File: 10_Dashboard_Client/results/step39_checks.csv; SHA-256 2DA3E3899E47A1C5... |
| DF74 | step40_checks.csv (13 checks of verify_step40.m) and step40_event_run.csv (the four sampling events of the full simulated day as the dashboard shows them: time, record_id, ML class, conventional methods agreeing, simulated hot-spot temperature). Use: Evidence for the Step 40 check: a full simulated day runs from the app. | File: 10_Dashboard_Client/results/step40_checks.csv; SHA-256 9CA8E7417EB4A616... |
| SW2 | MATLAB R2025b, version 25.2.0.2998904, The MathWorks, Inc., Natick, MA, USA. Use: Runs the conventional-method functions, unit tests, batch run and Duval figures (Steps 14-17). | https://www.mathworks.com/products/matlab.html |
| SW6 | FastAPI 0.143.0 (web framework), Uvicorn 0.54.0 (server), Pydantic 2.14.0 (input validation), HTTPX 0.28.1 (HTTP client for tests and the service check); Python packages pinned in 06_Python_ML/requirements.txt. Use: Runs the diagnosis service of Step 38 and its tests. | https://fastapi.tiangolo.com/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 15. How this helps the next steps

Next step: Step 43 (thesis): Thesis_Draft_v3.docx already contains the new dashboard section and Figure 8.6; the researcher should read it, confirm D43, and decide the open items (author name, repository licence).

•  The dashboard can now be shown to the supervisor with a healthy sample and every fault type in one run, and each result is explained in words and by the standard procedure.

•  Chapter 8 of the thesis (Thesis_Draft_v3.docx) describes the new screen and gives the descriptive result of the verdict; the plain-language document Project_Explained_Simply.docx explains the whole project.

# 16. Open items and limitations

•  D43 is proposed and needs the researcher's confirmation; the vote rule is a display rule, not a validated classifier.

•  The typical-value check lets 7 faults with very low gas levels pass as HEALTHY (typical values are not fault limits, IEC 60599 Annex A).

•  Not tested on a second computer; the screen was designed for a 1380 x 740 pixel window.

•  The numbers in the sample table are shown with four decimals (a limit of the App Designer table); they are not rounded in the data.

•  The recommended actions in the banner are general engineering practice, not requirements of IEC 60599 (TO VERIFY against the utility's own procedure).

•  No repository licence has been chosen; the IEEE DataPort raw files are not part of the repository copy (terms TO VERIFY).

# 17. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| D2 | discharges of high energy | Arcing with power follow-through: extensive carbonisation, metal fusion, sometimes tripping of the equipment. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| T2 | thermal fault 300 to 700 °C | Overheating in which the paper has carbonised. |
| T3 | thermal fault above 700 °C | Very hot fault: carbonised oil, metal colouring (800 °C) or metal fusion (above 1 000 °C). |
| DT | mixture of thermal and electrical faults | A zone of the Duval Triangle 1 for cases that look partly thermal and partly electrical. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEEE | Institute of Electrical and Electronics Engineers | A professional body that publishes engineering standards and journals. |
| IEEE C57.104 | IEEE guide for the interpretation of gases generated in oil-immersed transformers | The IEEE standard that contains the Duval Triangle 1 (2019 edition) and the Rogers ratio table (2008 edition). |
| Duval Triangle 1 | graphical DGA method by M. Duval | The shares of CH4, C2H4 and C2H2 are plotted as one point in a triangle divided into fault zones. |
| Rogers ratios | older gas-ratio method by R.R. Rogers | A ratio table that names faults from three gas ratios; kept in IEEE C57.104. |
| Typical values | 90 % typical gas concentrations | Levels below which about 90 % of transformers in service are found; not limit values. |
| Normality gate | rule that lets conventional methods answer 'Normal' | If all gases are below their typical values, the conventional methods give Normal instead of a fault (decision D3). |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Complete-case | records with all five gases reported | Used only for the sensitivity analysis. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Random seed | starting number for the random shuffle | Recording it means the same split can be made again exactly (seed 20261010). |
| Log scale | logarithmic axis | Each step on the axis is ten times the previous one, so very small and very large values fit on one chart. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| Simulink, Simscape | MATLAB's block-diagram modelling tool and its physical-modelling library | Used to model the transformer's operating conditions (Simulink Agentic Toolkit); it never makes gas values. |
| D1-D42 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| ND (no diagnosis) | No diagnosis | The answer of a method when no rule applies or a ratio it needs cannot be calculated. It is a result and is never deleted. |
| Dual answer (D1/D2) | Two classes returned together | Sometimes the IEC table fits two fault types at once. The method then answers with both (D1/D2); it counts as correct if the true class is either one. |
| Unit test (matlab.unittest) | Automatic test of one small piece of code | A test that feeds a function a known input and checks the answer, so that any later change that breaks the function is noticed at once. |
| Majority baseline | reference model | Always predicts the most common class; any useful model must do clearly better. |
| Class probability | model's confidence in each class | For every record the model gives a probability for each of the seven classes; they add up to 1 and the largest is the prediction. |
| Gas-level importance | shuffling one gas and everything made from it | One raw gas is shuffled before the features are built, so all its ratios and percentages move together; this avoids under-rating gases whose information is shared by several features. |
| Tolerance (delta) | largest acceptable loss | Fixed before the study at 0.05 macro-F1 (5 percentage points), approved in Step 4. |
| Simulink | MathWorks block-diagram simulation environment | Software in which the model is drawn as blocks and lines and simulated over time. |
| Hot-spot temperature | Temperature of the hottest part of the winding | The winding temperature that mostly decides how fast the paper insulation ages; it is the top-oil temperature plus a load-dependent rise. |
| Overload | Load above rated current | A load factor above 1.0 per unit; the hot spot heats quickly and the ageing rate rises steeply. |
| Sampling event | A moment in simulated time at which a gas sample would be taken | The model only says when; the gas values come from the real measured record in the data file, never from the model. |
| Held-out record | A record of the master table that is not used for development | A record kept aside (benchmark, internal test or external test) so that the methods are judged on data they did not learn from. |
| App Designer | MATLAB tool for building apps (.mlapp files) | The program in which DGADashboard.mlapp is edited; the file can also be run without opening it. |
| HTTP | Hypertext Transfer Protocol | The message format of the web; the dashboard sends a request and the service sends back an answer with a status code (200 = OK, 422 = input refused). |
| FastAPI | Python framework for web services | The library used to build the diagnosis service; it also checks every input against the declared rules. |
| Test bench | the integrated system run over every held-out record | Simulink model, MATLAB dashboard functions and the Python service working together, with every answer and its time written to a log (Step 41). |