Step 4 Report

Approve the decisions and the analysis plan

Environment: Approval gate (researcher)   |   Completed: 10 October 2026   |   Report version 2 (11 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The researcher approved the plan and all 18 items of the analysis plan on 10 October 2026, on the condition that every step follows standard research procedure. This is recorded as the researcher's approval; the supervisor's sign-off is not yet recorded.

# 1. Purpose of this step

Fixing the decisions and the analysis method before any data is analysed prevents choosing methods after seeing the results. This is a recognised safeguard for honest research.

# 2. Method used

## Approach

Pre-specification: every analysis choice - which data play which role, which measures and statistical tests are used, the tolerances and the figures - was written into the Expected Results and Analysis Plan and approved before any data were analysed. Any later change is allowed only as a numbered decision with its evidence in the decision log.

## Why this method

•  Fixing the methods before seeing the results prevents choosing, consciously or not, the method that gives the best-looking result.

•  A written decision log lets supervisors, examiners and reviewers check that every change was justified by evidence (as for D8 and D9).

## Settings and rules

| Setting | Value |
| --- | --- |
| Items approved | 18 analysis-plan items (Section 14 of the Analysis Plan) |
| Decisions handled | D1-D7 (D5 left open); later D8, D9, D10 added with evidence |
| Approver | The researcher (supervisor sign-off not yet recorded) |

## Tools and programs

•  00_Project_Admin/Expected_Results_and_Analysis_Plan.docx; Project_Roadmap.docx; decisions_log.md

# 3. What was done, step by step

1.  The researcher reviewed the roadmap and the Expected Results and Analysis Plan and approved them.

2.  Each open decision (D1 to D7) was closed with the proposed resolution, except D5, which is a fact only the researcher can confirm.

3.  For decision D6 (the fifth classifier) multinomial logistic regression was chosen: it is the standard simple and explainable baseline and is a different kind of model from the other four.

4.  Everything was written into 00_Project_Admin/decisions_log.md, which is the single record of all decisions.

# 4. The decisions

| No. | Decision | Status |
| --- | --- | --- |
| D1 | Thesis Chapter 1 objectives govern; the reduced-gas study is an added study. | Closed |
| D2 | Five gases (H2, CH4, C2H6, C2H4, C2H2); CO and CO2 not used. | Closed |
| D3 | Normal kept as class 0 where present; a normality gate lets conventional methods output Normal. | Closed |
| D4 | Simulink models only the operating context; it never makes gas values. | Closed |
| D5 | Author name and degree differ between the two original documents. | Open (not blocking) |
| D6 | Classifiers: SVM, Random Forest, XGBoost, MLP, logistic regression (plus a majority baseline). | Closed |
| D7 | Dissanayake training data used for training only if its labels are not inspection-based. | Closed in Step 9 with evidence |
| D8 | Not-available gas values treated as not detected (0 ppm) - added in Step 6, replaces plan item 4. | Closed |
| D9 | Test records that copy benchmark cases are flagged - added in Step 9. | Closed |

# 5. Problems and fixes

None at this step. Two later decisions (D8 and D9) were added when the data showed they were needed; each is explained in its own step report.

# 6. Files produced

•  00_Project_Admin/decisions_log.md

# 7. What was achieved

•  The plan and all 18 analysis-plan items were approved before any data were analysed.

•  Decisions D1-D4 and D6 were closed; D5 was left open because only the researcher can confirm it.

•  One single record of every decision now exists (00_Project_Admin/decisions_log.md).

# 8. Record of this step

| Item | Record |
| --- | --- |
| Step | 4 - Approve the decisions and the analysis plan |
| Environment | Approval gate (researcher) |
| Completed | 10 October 2026 |
| Status | Done (researcher's approval; supervisor sign-off not yet recorded) |
| Main inputs | Project_Roadmap.docx; Expected_Results_and_Analysis_Plan.docx |
| Main outputs | 00_Project_Admin/decisions_log.md |
| Checks | Every open decision has a recorded outcome |
| Decisions | D1-D4 and D6 closed; D5 open; D8 and D9 added later |

# 9. Data and sources used in this step

No dataset or external source was used in this step. The step approved two project documents: 00_Project_Admin/Project_Roadmap.docx and 00_Project_Admin/Expected_Results_and_Analysis_Plan.docx.

# 10. How this helps the next steps

Next step: Step 5: load and standardise the raw datasets.

•  Every later step follows rules that were fixed in advance (which data, which measures, which tests), so results cannot be shaped after seeing them. Reviewers and examiners can check this.

•  When the data later showed that a rule had to change (missing values, D8), the change was made openly, with evidence, and recorded - instead of silently.

# 11. Open items and limitations

•  The supervisor's sign-off is not yet recorded.

•  D5 (author name and degree differ between the two original documents) is open but does not block the work.

•  The Analysis Plan document still has to be updated with D8, D9 and the Step 12 source facts (one combined update is planned).

# 12. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| CH4 | methane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H6 | ethane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H4 | ethylene | Hydrocarbon gas favoured above about 500 °C; it rises as thermal faults get hotter. |
| C2H2 | acetylene | Gas that needs at least 800 to 1 200 °C; formed in significant amounts mainly in electrical arcs. |
| CO, CO2 | carbon monoxide, carbon dioxide | Gases formed mainly when paper insulation breaks down; not used in this thesis (decision D2). |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| Normality gate | rule that lets conventional methods answer 'Normal' | If all gases are below their typical values, the conventional methods give Normal instead of a fault (decision D3). |
| SVM | support vector machine | A classifier that separates classes with the widest possible boundary. |
| Random Forest | random forest | Many decision trees, each trained on a random sample; they vote for the answer. |
| XGBoost | extreme gradient boosting | Decision trees built one after another, each correcting the errors of the previous ones. |
| MLP | multilayer perceptron | A small artificial neural network with layers of connected units. |
| Logistic regression | multinomial logistic regression | A simple, explainable model that turns weighted gas values into class probabilities. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Not detected | gas below the laboratory's detection limit | Treated as 0 ppm in this thesis (decision D8). |
| docx | Microsoft Word document | The format of these reports. |
| Simulink, Simscape | MATLAB's block-diagram modelling tool and its physical-modelling library | Used to model the transformer's operating conditions (Simulink Agentic Toolkit); it never makes gas values. |
| D1-D11 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |