Step 5 Report

Load and standardise the raw datasets

Environment: Claude Code (this chat)   |   Completed: 10 October 2026   |   Report version 2 (11 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: All five data files were checked against their recorded fingerprints, read without being changed, and rewritten in one common layout. All checks passed. Two important problems were discovered in the Dissanayake files: a fake value (0.0001) used where a gas value was missing, and copies of the IEC TC 10 benchmark cases inside the training file.

# 1. Purpose of this step

The datasets come from different places and use different column names and orders. Before anything else, every file must be checked to be exactly the file that was downloaded, and then put into one common layout so all later steps can treat them the same way.

# 2. Method used

## Approach

Integrity check: the SHA-256 fingerprint of every raw file was calculated and compared with the value recorded at download.

Faithful reading: every file was read as plain text, so that the reading software could not silently change any value (for example, turn an empty cell into a number). Values were then converted to numbers one by one, and any value that could not be converted was reported.

Standardisation: the columns were renamed and put into one shared order, every record received a unique identifier and the line number in its source file, and every re-ordered cell was compared with the original.

## Why this method

•  Checking fingerprints proves that the data analysed are exactly the published data (data integrity).

•  Keeping the source line number makes every record traceable to its origin, which is needed to find copies later (Step 9).

•  Converting values explicitly, rather than trusting automatic conversion, means no value is changed without being reported.

## Settings and rules

| Setting | Value |
| --- | --- |
| Gas order | H2, CH4, C2H6, C2H4, C2H2 (unit: ppm) |
| Record identifier | SOURCE_NNNN, e.g. DISTRAIN_0001, plus source file and line number |
| Empty cells | kept as missing - never replaced in this step |
| Impossible values checked | negative numbers and text that is not a number |
| Fingerprint algorithm | SHA-256 |

## Tools and programs

•  06_Python_ML/src/data_prep/step05_standardise.py

•  pandas 3.0.6 (read_csv / read_excel with dtype=str and keep_default_na=False; openpyxl 3.1.5 for Excel); Python hashlib for SHA-256

## Method references

[M1] National Institute of Standards and Technology, "Secure Hash Standard (SHS)," FIPS PUB 180-4, Aug. 2015. doi: 10.6028/NIST.FIPS.180-4

# 3. What was used

•  The five raw files in 03_Data/raw: the IEC TC 10 table transcribed from Duval and dePablo (2001), the three Dissanayake files (training, unseen test, IEC subset) and the Li (2019) file.

•  The fingerprints (SHA-256 hashes) recorded in the data cards when the files were downloaded.

# 4. What was done, step by step

1.  Calculated the SHA-256 fingerprint of each file and compared it with the data card. A different fingerprint would mean the file had changed.

2.  Read each file without changing it. The Li file has three sheets; the second and third were opened and confirmed to be empty.

3.  Renamed and re-ordered the gas columns into the shared order H2, CH4, C2H6, C2H4, C2H2. The IEC table stores the gases in a different order, so every one of its 585 gas cells was compared with the original afterwards to make sure nothing was moved to the wrong column.

4.  Gave every record a unique identifier (for example DISTRAIN_0001), and noted its source file and line number, so any record can be traced back to the original.

5.  Kept empty cells as missing - never replaced by zero. Counted zeros, empty cells and impossible values (negative or non-numeric).

6.  Wrote the fingerprints of all raw files into 03_Data/raw/checksums.sha256.

# 5. What we found

| Source | Records (expected) | Fingerprint | Records with all 5 gases | Repeated rows |
| --- | --- | --- | --- | --- |
| IEC TC 10 (transcription) | 117 (117) | recorded for the first time | 99 | 0 |
| Dissanayake training | 584 (584) | matches | 584 | 2 |
| Dissanayake unseen test | 70 (70) | matches | 70 | 0 |
| Dissanayake IEC subset | 49 (49) | matches | 49 | 0 |
| Li 2019 | 201 (201) | matches | 201 | 0 |

Further findings from a closer look at the values:

•  The value 0.0001 ppm appears 257 times in the Dissanayake training file and 34 times in its test file. Such a tiny value cannot be measured by any laboratory, so it is a stand-in for 'no value available', not a measurement.

•  The two repeated rows in the Dissanayake training file are IEC TC 10 cases. For example, lines 111 and 137 are both the IEC case 'Short circuit from LV to ground, internal'; where the paper prints a dash for ethane, the file has 0.0001.

•  The Dissanayake IEC subset is not purely the paper's Annex 1: it contains 15 Normal records (Annex 1 has none) and decimal values such as 0.7, while every Annex 1 value is a whole number.

•  The IEC transcription has 23 empty cells (dashes in the paper): H2 1, CH4 1, C2H6 7, C2H4 3, C2H2 11.

# 6. Checks

•  All fingerprints match the data cards - PASS.

•  All record counts match: 117; 584, 70 and 49; 201 - PASS.

•  IEC column re-ordering: 0 mismatches in 585 gas cells - PASS.

•  No negative or non-numeric gas values - PASS.

# 7. Problems and fixes

No processing problem. The data problems found (placeholder values and copied benchmark cases) were left untouched in this step - its job is to copy faithfully - and were passed to Steps 6 and 9, where they are handled. They were also written into the data cards.

# 8. Files produced

•  03_Data/interim/IECTC10_standardised.csv, DISTRAIN_, DISTEST_, DISIEC_ and LI2019_standardised.csv

•  03_Data/interim/step05_report.md and 03_Data/raw/checksums.sha256

•  Program: 06_Python_ML/src/data_prep/step05_standardise.py

# 9. What was achieved

•  All five raw files were proven unchanged since download (fingerprints match).

•  1 021 records (117 + 584 + 70 + 49 + 201) are now in one common layout with the same gas order and a unique, traceable identifier.

•  Two data problems were found early: the 0.0001 placeholder values and copies of benchmark cases inside the training file.

# 10. Record of this step

| Item | Record |
| --- | --- |
| Step | 5 - Load and standardise the raw datasets |
| Environment | Claude Code (this chat) |
| Completed | 10 October 2026 |
| Status | Done |
| Main inputs | The five raw files in 03_Data/raw and their data cards |
| Main outputs | 03_Data/interim/*_standardised.csv; checksums.sha256; step05_report.md |
| Checks | Fingerprints, record counts, 585 re-ordered IEC cells, no impossible values - all PASS |
| Decisions | None (problems passed to Steps 6 and 9) |

# 11. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DS1 | M. Duval and A. dePablo, "Interpretation of gas-in-oil analysis using new IEC publication 60599 and IEC TC 10 databases," IEEE Electrical Insulation Magazine, vol. 17, no. 2, pp. 31-41, Mar./Apr. 2001. Use: Main benchmark (labels confirmed by inspection): primary analysis = 58 power transformers (codes P, U); sensitivity = all 117. | https://doi.org/10.1109/57.917529; DOI 10.1109/57.917529; File: 03_Data/raw/iec_tc10_duval2001_full/iec_tc10_faulty_equipment.csv; SHA-256 EF9F6B542821264A... |
| DS2 | T. Dissanayake, "DGA dataset," IEEE DataPort, 2026. Use: Development (training) set: 439 records after removing leakage and copies (Step 9). | https://ieee-dataport.org/documents/dga-dataset; DOI 10.21227/27vy-h479; File: 03_Data/raw/ieee_dataport_1375187/DGA_train.xlsx; SHA-256 C1C376718D72A747... |
| DS3 | T. Dissanayake, "DGA dataset," IEEE DataPort, 2026. Use: Internal test set: 61 records independent of the benchmark (primary); all 70 as sensitivity. | https://ieee-dataport.org/documents/dga-dataset; DOI 10.21227/27vy-h479; File: 03_Data/raw/ieee_dataport_1375187/DGA_test_unseen.xlsx; SHA-256 23513C428C52F3BD... |
| DS4 | T. Dissanayake, "DGA dataset," IEEE DataPort, 2026. Use: Not used in any role: replaced by our full transcription DS1 (only 31 of its 49 rows match Annex 1). | https://ieee-dataport.org/documents/dga-dataset; DOI 10.21227/27vy-h479; File: 03_Data/raw/ieee_dataport_1375187/IEC_TC_10_data.xlsx; SHA-256 2B5B128ABF38533E... |
| DS5 | E. Li, "Dissolved gas data in transformer oil - Fault Diagnosis of Power Transformers with Membership Degree," IEEE DataPort, 2019. Use: External test set: 86 records independent of the benchmark (primary); all 201 as sensitivity. | https://ieee-dataport.org/documents/dissolved-gas-data-transformer-oil-fault-diagnosis-power-transformers-membership-degree; DOI 10.21227/h8g0-8z59; File: 03_Data/raw/ieee_dataport_7226/DGA dataset.xlsx; SHA-256 B797638252DB69C0... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 12. How this helps the next steps

Next step: Step 6: record the missing values and decide how to treat them.

•  Step 6 can count missing values with one program for all sources, because all files now look the same.

•  Step 9 uses the record identifiers and original line numbers to trace every copy back to its source.

•  The fingerprints are the basis of the data freeze in Step 13: every later result can be traced to these exact files.

# 13. Open items and limitations

•  None - the problems found were handled in Steps 6 and 9.

# 14. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| CH4 | methane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H6 | ethane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H4 | ethylene | Hydrocarbon gas favoured above about 500 °C; it rises as thermal faults get hotter. |
| C2H2 | acetylene | Gas that needs at least 800 to 1 200 °C; formed in significant amounts mainly in electrical arcs. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| LV, HV | low voltage, high voltage | The lower- and higher-voltage sides (windings, connections) of a transformer. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| IEEE | Institute of Electrical and Electronics Engineers | A professional body that publishes engineering standards and journals. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Internal test set | Dissanayake unseen test file | 70 records (61 independent of the benchmark) kept away from training. |
| External test set | Li (2019) dataset | 201 records from a different source (86 independent of the benchmark), used to test the models on new data. |
| Placeholder (0.0001) | stand-in value | A fake tiny number written where no measurement was available; treated as not detected (D8). |
| Leakage | test cases hidden in the training data | If a model has already seen a test case, its score is falsely high. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| Data card | provenance record of a dataset | States where a dataset came from, its licence, its fingerprint and known problems. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |