Step 7 Report

Harmonise the fault labels

Environment: Claude Code (this chat)   |   Completed: 10 October 2026   |   Report version 2 (11 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: Every original fault label in every dataset was translated into one shared set of codes, with a written reason for each translation. All labels were translated and the counts match the data cards.

# 1. Purpose of this step

The datasets name faults differently: Dissanayake uses numbers 0 to 6, the IEC tables use PD, D1, D2, T1/T2 and T3, and Li uses words such as 'Spark discharge'. All methods must be judged against the same labels.

# 2. Method used

## Approach

Label harmonisation with an explicit translation table (label map): one row for every original label in every file, giving the new class code, the reason and the evidence. The table is applied automatically to every record; a label that is not in the table stops the program.

## Why this method

•  All methods must be judged against the same class definitions; the definitions follow IEC 60599, clause 5.2.

•  A written table with reasons makes every translation open to checking, instead of being hidden inside code.

•  Where a source cannot separate two classes (T1 and T2 in IEC TC 10), they are merged (T12) rather than guessed.

## Settings and rules

| Setting | Value |
| --- | --- |
| Fine scheme | 0 Normal, 1 PD, 2 D1, 3 D2, 4 T1, 5 T2, 6 T3 |
| Merged scheme | T1 and T2 joined as T12 (used for the IEC TC 10 benchmark) |
| Rows in the label map | 33 (7 for each Dissanayake file, 5 IEC TC 10, 7 Li 2019) |
| Unknown labels | not allowed - the program stops |

## Tools and programs

•  06_Python_ML/src/data_prep/step07_label_map.py (pandas 3.0.6); output 03_Data/processed/label_map.csv

## Method references

[ST1] IEC 60599:1999+A1:2007, Mineral oil-impregnated electrical equipment in service - Guide to the interpretation of dissolved and free gases analysis, Ed. 2.1. Geneva: IEC, 2007. https://standards.iteh.ai/catalog/standards/iec/31551405-c771-4a06-b021-4c2433c11fb9/iec-60599-1999

[DS1] M. Duval and A. dePablo, "Interpretation of gas-in-oil analysis using new IEC publication 60599 and IEC TC 10 databases," IEEE Electrical Insulation Magazine, vol. 17, no. 2, pp. 31-41, Mar./Apr. 2001. doi: 10.1109/57.917529

# 3. What was done, step by step

1.  Defined the shared fine scheme: 0 Normal, 1 PD, 2 D1, 3 D2, 4 T1, 5 T2, 6 T3.

2.  Defined a merged scheme in which T1 and T2 are joined as T12, for records whose source does not say whether the fault was below or above 300 degrees C.

3.  Wrote a label map with one row for every original label, its new code, the reason and the evidence.

4.  Applied the map to every record and counted the records per class.

# 4. The label map in plain words

•  Dissanayake: codes used as given on the dataset's web page.

•  IEC TC 10: PD, D1, D2 and T3 map directly; 'T1/T2' maps to the merged class T12 because the paper puts both in one table without saying which is which.

•  Li 2019: partial discharge = PD; spark discharge = D1 (low energy); arc discharge = D2 (high energy); low-, middle- and high-temperature overheating = T1, T2 and T3; 'low/middle-temperature overheating' = T12. The spark/arc rule follows the IEC paper itself, which lists sparking cases under D1 and arcing cases under D2. (Step 9 later confirmed this mapping against the IEC cases.)

# 5. What we found

| Source | Records | Normal | PD | D1 | D2 | T1 | T2 | T12 | T3 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| IEC TC 10 | 117 | 0 | 9 | 26 | 48 | 0 | 0 | 16 | 18 |
| Dissanayake training | 584 | 85 | 59 | 76 | 134 | 96 | 45 | 0 | 89 |
| Dissanayake test | 70 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 |
| Dissanayake IEC subset | 49 | 15 | 1 | 7 | 15 | 1 | 2 | 0 | 8 |
| Li 2019 | 201 | 0 | 16 | 49 | 54 | 19 | 9 | 16 | 38 |

# 6. Checks

Every original label in every file maps to exactly one row of the label map; no record was left without a class - PASS. The counts equal those in the data cards.

# 7. Files produced

•  03_Data/processed/label_map.csv (33 rows: 7 for each of the three Dissanayake files, 5 for IEC TC 10, 7 for Li 2019; each with its reason and evidence)

•  03_Data/interim/<source>_step07.csv and step07_report.md; program step07_label_map.py

# 8. What was achieved

•  Every original fault label in the five files (33 rows in the label map) was translated into one shared scheme (0 Normal, 1 PD, 2 D1, 3 D2, 4 T1, 5 T2, 6 T3, plus the merged class T12).

•  Every translation has a written reason and evidence (label_map.csv).

•  Every record received a class; the class counts equal those in the data cards.

# 9. Record of this step

| Item | Record |
| --- | --- |
| Step | 7 - Harmonise the fault labels |
| Environment | Claude Code (this chat) |
| Completed | 10 October 2026 |
| Status | Done |
| Main inputs | *_step06.csv (Step 6); dataset web pages; Duval and dePablo (2001) |
| Main outputs | 03_Data/processed/label_map.csv (33 rows); *_step07.csv; step07_report.md |
| Checks | Every label maps to exactly one class; no record left unlabelled - PASS |
| Decisions | None |

# 10. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DS1 | M. Duval and A. dePablo, "Interpretation of gas-in-oil analysis using new IEC publication 60599 and IEC TC 10 databases," IEEE Electrical Insulation Magazine, vol. 17, no. 2, pp. 31-41, Mar./Apr. 2001. Use: Main benchmark (labels confirmed by inspection): primary analysis = 58 power transformers (codes P, U); sensitivity = all 117. | https://doi.org/10.1109/57.917529; DOI 10.1109/57.917529; File: 03_Data/raw/iec_tc10_duval2001_full/iec_tc10_faulty_equipment.csv; SHA-256 EF9F6B542821264A... |
| DS2 | T. Dissanayake, "DGA dataset," IEEE DataPort, 2026. Use: Development (training) set: 439 records after removing leakage and copies (Step 9). | https://ieee-dataport.org/documents/dga-dataset; DOI 10.21227/27vy-h479; File: 03_Data/raw/ieee_dataport_1375187/DGA_train.xlsx; SHA-256 C1C376718D72A747... |
| DS3 | T. Dissanayake, "DGA dataset," IEEE DataPort, 2026. Use: Internal test set: 61 records independent of the benchmark (primary); all 70 as sensitivity. | https://ieee-dataport.org/documents/dga-dataset; DOI 10.21227/27vy-h479; File: 03_Data/raw/ieee_dataport_1375187/DGA_test_unseen.xlsx; SHA-256 23513C428C52F3BD... |
| DS4 | T. Dissanayake, "DGA dataset," IEEE DataPort, 2026. Use: Not used in any role: replaced by our full transcription DS1 (only 31 of its 49 rows match Annex 1). | https://ieee-dataport.org/documents/dga-dataset; DOI 10.21227/27vy-h479; File: 03_Data/raw/ieee_dataport_1375187/IEC_TC_10_data.xlsx; SHA-256 2B5B128ABF38533E... |
| DS5 | E. Li, "Dissolved gas data in transformer oil - Fault Diagnosis of Power Transformers with Membership Degree," IEEE DataPort, 2019. Use: External test set: 86 records independent of the benchmark (primary); all 201 as sensitivity. | https://ieee-dataport.org/documents/dissolved-gas-data-transformer-oil-fault-diagnosis-power-transformers-membership-degree; DOI 10.21227/h8g0-8z59; File: 03_Data/raw/ieee_dataport_7226/DGA dataset.xlsx; SHA-256 B797638252DB69C0... |
| DF1 | Made in Step 7 from DS1-DS5 and the dataset pages. Use: Translation of every original fault label into the shared scheme. | File: 03_Data/processed/label_map.csv; SHA-256 F66465BFB7BFB445... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 11. How this helps the next steps

Next step: Step 8: keep only power transformers for the main benchmark.

•  All methods - conventional and machine learning - are judged against the same labels, so their scores can be compared fairly.

•  The merged scheme (with T12) is the one used to score the IEC TC 10 benchmark, because that source does not separate T1 from T2.

•  Step 9 later confirmed the Li 2019 mapping on 115 cases that also appear in IEC TC 10 (115 of 115 agree).

# 12. Open items and limitations

•  Correction recorded on 10 October 2026: the first version of this report said the label map has 25 rows. Re-counting the file shows 33 rows (7 for each of the three Dissanayake files, 5 for IEC TC 10, 7 for Li 2019). The data were never affected; only the number in the text was wrong, and it is now corrected here and in the CHANGELOG.

# 13. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| D2 | discharges of high energy | Arcing with power follow-through: extensive carbonisation, metal fusion, sometimes tripping of the equipment. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| T2 | thermal fault 300 to 700 °C | Overheating in which the paper has carbonised. |
| T3 | thermal fault above 700 °C | Very hot fault: carbonised oil, metal colouring (800 °C) or metal fusion (above 1 000 °C). |
| T12 | T1 or T2 (merged class) | Used in this project when a source does not say whether the thermal fault was below or above 300 °C. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| IEEE | Institute of Electrical and Electronics Engineers | A professional body that publishes engineering standards and journals. |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Internal test set | Dissanayake unseen test file | 70 records (61 independent of the benchmark) kept away from training. |
| External test set | Li (2019) dataset | 201 records from a different source (86 independent of the benchmark), used to test the models on new data. |
| Leakage | test cases hidden in the training data | If a model has already seen a test case, its score is falsely high. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| Data card | provenance record of a dataset | States where a dataset came from, its licence, its fingerprint and known problems. |
| Label map | translation table of fault labels | Lists every original label, its new code and the reason. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |