Step 9 Report

Remove duplicates and audit leakage

Environment: Claude Code (this chat)   |   Completed: 10 October 2026   |   Report version 2 (11 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The training data contained 96 of the IEC TC 10 benchmark cases and other copies of test records; 139 such records were removed from training so that no test case can be learned in advance. The audit also showed that Li 2019 is mostly a copy of IEC TC 10, and that some Dissanayake labels contradict the inspection results. The final clean table has 827 records and passes all automated leakage checks.

# 1. Purpose of this step

If a test case also sits in the training data, the model has seen the answer and its score is falsely high - this is called leakage. This step finds every copy and near-copy and removes them from the training data.

# 2. Method used

## Approach

Record linkage by rules fixed in advance. Gas values were first harmonised with decision D8. Two records were called an exact match if all five gases are equal (rounded to 4 decimals), and a near match if every gas differs by no more than the tolerance in Equation 1.

Within each file, exact copies were reduced to the first one; if identical gases carried different labels, all copies were removed. Across files, every record was compared with every other record. A training record that matches any test record (exactly or nearly) was removed from training. Overlaps between test sets were flagged, not removed.

Where a training or test record copies an IEC TC 10 case, its label was compared with the inspection label (label-agreement analysis).

## Why this method

•  If a test case is also in the training data, the model has seen the answer and its score is falsely high. Such leakage is a documented cause of irreproducible machine-learning results (Kapoor and Narayanan, 2023).

•  The near-match rule also catches copies that differ only by rounding or by the 0.0001 placeholder.

•  Comparing labels with inspection results measures how trustworthy each dataset's labels are.

## Settings and rules

| Setting | Value |
| --- | --- |
| Relative tolerance | 1 % of the larger value |
| Absolute tolerance | 1 ppm |
| Exact match | all five gases equal after rounding to 4 decimals |
| Duplicates within a file | keep the first (lowest source line); remove all if labels conflict |
| Overlaps between test sets | flagged (decision D9), never removed |

## Equations

ag-bg≤max1 ppm,0.01⋅maxag,bg  for every gas g#1

where:

ag, bg  –  concentration of gas g in the two records being compared [ppm]

g  –  each of the five gases H2, CH4, C2H6, C2H4, C2H2

## Tools and programs

•  06_Python_ML/src/data_prep/step09_dedup_leakage.py (numpy 2.5.3 pairwise comparison, pandas 3.0.6)

•  06_Python_ML/tests/test_no_leakage.py (pytest 9.1.1, 5 automated tests)

## Method references

[M2] S. Kapoor and A. Narayanan, "Leakage and the reproducibility crisis in machine-learning-based science," Patterns, vol. 4, no. 9, art. 100804, 2023. doi: 10.1016/j.patter.2023.100804

# 3. The rules (fixed before looking at the results)

1.  Gas values are compared after applying decision D8 (dash, 0.0001 and 0 all mean not detected), so that a copy is recognised even when a dash became 0.0001.

2.  Exact copy within one file: keep the first. If identical gases carry different labels, remove all of them, because the true label cannot be known.

3.  A training record that matches any test record exactly, or nearly (every gas within 1 percent or 1 ppm), is removed from the training data.

4.  Overlaps between test sets are reported and flagged, not removed.

5.  The Dissanayake IEC subset is not used, because our full transcription of the paper replaces it; its origin is still traced.

# 4. What we found

| Sources compared | Exact matches | Near matches |
| --- | --- | --- |
| IEC TC 10 and Dissanayake training | 96 | 0 |
| IEC TC 10 and Li 2019 | 115 | 0 |
| IEC TC 10 and Dissanayake test | 9 | 0 |
| Dissanayake training and Li 2019 | 125 | 4 |
| Dissanayake training and Dissanayake test | 1 | 21 |
| Dissanayake test and Li 2019 | 10 | 0 |

•  Removed from training: 139 records for leakage (96 matching IEC TC 10, 35 matching Li 2019, 8 matching the unseen test file), 2 exact copies, and 4 records whose identical gas values carried different labels. Training data left: 439 records.

•  Li 2019 contains 115 of the 117 IEC TC 10 cases, and for all 115 its labels agree with the inspection labels. Its 16 'low/middle-temperature' records are exactly the paper's 16 T1/T2 cases. This confirms the label mapping of Step 7. Only 86 Li records are independent of the benchmark.

•  Where Dissanayake copied IEC cases, its label agrees with the inspection label in 132 of 136 cases. The 4 disagreements are cases the paper calls 'thermal below 700 degrees C' that Dissanayake labelled T3 (above 700 degrees C, 3 cases) or PD (1 case). These labels cannot have come from the inspection, so part of the Dissanayake labelling was done another way, probably with a ratio method.

•  The Dissanayake IEC subset: 31 of its 49 rows match the paper; 18 do not, including its 15 Normal rows.

# 5. Decisions

•  D7 closed with this evidence: the Dissanayake data is used for training only; its unseen test file is supporting evidence; the inspection-labelled IEC TC 10 set remains the main benchmark.

•  D9 (standard practice): test records that copy a benchmark case are flagged. Results reported as separate evidence use only independent records - 61 of 70 in the internal test and 86 of 201 in Li 2019; the full sets are reported as a sensitivity analysis.

# 6. The clean master table

| Data role | Normal | PD | D1 | D2 | T1/T2 (T12) | T3 | Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Development (training) | 75 | 37 | 53 | 85 | 119 (T1 80, T2 39) | 70 | 439 |
| Internal test | 10 | 10 | 10 | 10 | 20 (T1 10, T2 10) | 10 | 70 |
| IEC TC 10 benchmark | 0 | 9 | 26 | 48 | 16 | 18 | 117 |
| External test (Li 2019) | 0 | 16 | 49 | 54 | 44 | 38 | 201 |

# 7. Checks

•  No training record matches any test record, exactly or nearly - PASS.

•  Automated test program 06_Python_ML/tests/test_no_leakage.py (5 tests: unique identifiers, valid roles and classes, complete non-negative gases, no training-test match, no copies within a role) - 5 of 5 passed.

# 8. Problems and fixes

Two summary tables again lost rows whose label was empty (the same software behaviour as in Step 8). Both were fixed and the step re-run before it was accepted; the data itself was never affected.

# 9. Files produced

•  03_Data/processed/dga_master.csv (827 records; harmonised gases plus the original values for tracing)

•  03_Data/interim/duplicate_report.csv, label_agreement_iec.csv, step09_report.md; program step09_dedup_leakage.py

# 10. What was achieved

•  A clean master table of 827 records with a fixed role for each (development 439, internal test 70, benchmark 117, external test 201).

•  No training record matches any test record, exactly or nearly - the test scores later will be honest.

•  Evidence about label quality: Li 2019 agrees with the inspections on 115 of 115 cases; Dissanayake contradicts them on 4 cases (decision D7 closed).

•  Test records that copy benchmark cases are flagged, giving independent subsets (61 internal, 86 external) - decision D9.

# 11. Record of this step

| Item | Record |
| --- | --- |
| Step | 9 - Remove duplicates and audit leakage |
| Environment | Claude Code (this chat) |
| Completed | 10 October 2026 |
| Status | Done |
| Main inputs | *_step08.csv (Step 8) |
| Main outputs | 03_Data/processed/dga_master.csv; duplicate_report.csv; label_agreement_iec.csv; step09_report.md |
| Checks | No training-test match; automated tests 5 of 5 PASS |
| Decisions | D7 closed with evidence; D9 added |

# 12. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DS1 | M. Duval and A. dePablo, "Interpretation of gas-in-oil analysis using new IEC publication 60599 and IEC TC 10 databases," IEEE Electrical Insulation Magazine, vol. 17, no. 2, pp. 31-41, Mar./Apr. 2001. Use: Main benchmark (labels confirmed by inspection): primary analysis = 58 power transformers (codes P, U); sensitivity = all 117. | https://doi.org/10.1109/57.917529; DOI 10.1109/57.917529; File: 03_Data/raw/iec_tc10_duval2001_full/iec_tc10_faulty_equipment.csv; SHA-256 EF9F6B542821264A... |
| DS2 | T. Dissanayake, "DGA dataset," IEEE DataPort, 2026. Use: Development (training) set: 439 records after removing leakage and copies (Step 9). | https://ieee-dataport.org/documents/dga-dataset; DOI 10.21227/27vy-h479; File: 03_Data/raw/ieee_dataport_1375187/DGA_train.xlsx; SHA-256 C1C376718D72A747... |
| DS3 | T. Dissanayake, "DGA dataset," IEEE DataPort, 2026. Use: Internal test set: 61 records independent of the benchmark (primary); all 70 as sensitivity. | https://ieee-dataport.org/documents/dga-dataset; DOI 10.21227/27vy-h479; File: 03_Data/raw/ieee_dataport_1375187/DGA_test_unseen.xlsx; SHA-256 23513C428C52F3BD... |
| DS4 | T. Dissanayake, "DGA dataset," IEEE DataPort, 2026. Use: Not used in any role: replaced by our full transcription DS1 (only 31 of its 49 rows match Annex 1). | https://ieee-dataport.org/documents/dga-dataset; DOI 10.21227/27vy-h479; File: 03_Data/raw/ieee_dataport_1375187/IEC_TC_10_data.xlsx; SHA-256 2B5B128ABF38533E... |
| DS5 | E. Li, "Dissolved gas data in transformer oil - Fault Diagnosis of Power Transformers with Membership Degree," IEEE DataPort, 2019. Use: External test set: 86 records independent of the benchmark (primary); all 201 as sensitivity. | https://ieee-dataport.org/documents/dissolved-gas-data-transformer-oil-fault-diagnosis-power-transformers-membership-degree; DOI 10.21227/h8g0-8z59; File: 03_Data/raw/ieee_dataport_7226/DGA dataset.xlsx; SHA-256 B797638252DB69C0... |
| DF1 | Made in Step 7 from DS1-DS5 and the dataset pages. Use: Translation of every original fault label into the shared scheme. | File: 03_Data/processed/label_map.csv; SHA-256 F66465BFB7BFB445... |
| DF2 | Made in Step 9 from DS1-DS5 (Steps 5-9 programs). Use: All clean records with role, class, flags and original values. | File: 03_Data/processed/dga_master.csv; SHA-256 AE9E6C0C84CF7180... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 13. How this helps the next steps

Next step: Step 10: fix the cross-validation folds.

•  Step 10 splits only clean training data into folds.

•  Every score reported later (internal test, external test, benchmark) is free of leakage, which is a basic requirement for a fair and publishable evaluation.

•  The label-quality evidence supports the choice of the inspection-based IEC TC 10 set as the main benchmark.

# 14. Open items and limitations

•  None.

# 15. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| D2 | discharges of high energy | Arcing with power follow-through: extensive carbonisation, metal fusion, sometimes tripping of the equipment. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| T2 | thermal fault 300 to 700 °C | Overheating in which the paper has carbonised. |
| T3 | thermal fault above 700 °C | Very hot fault: carbonised oil, metal colouring (800 °C) or metal fusion (above 1 000 °C). |
| T12 | T1 or T2 (merged class) | Used in this project when a source does not say whether the thermal fault was below or above 300 °C. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| IEEE | Institute of Electrical and Electronics Engineers | A professional body that publishes engineering standards and journals. |
| Ratio method | diagnosis from gas ratios | Divides one gas by another (for example C2H2/C2H4) and compares the result with fixed limits to name the fault. |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Internal test set | Dissanayake unseen test file | 70 records (61 independent of the benchmark) kept away from training. |
| External test set | Li (2019) dataset | 201 records from a different source (86 independent of the benchmark), used to test the models on new data. |
| Placeholder (0.0001) | stand-in value | A fake tiny number written where no measurement was available; treated as not detected (D8). |
| Not detected | gas below the laboratory's detection limit | Treated as 0 ppm in this thesis (decision D8). |
| Leakage | test cases hidden in the training data | If a model has already seen a test case, its score is falsely high. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| Complete-case | records with all five gases reported | Used only for the sensitivity analysis. |
| Label map | translation table of fault labels | Lists every original label, its new code and the reason. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Cross-validation | repeated train-and-test on parts of the training data | The data are split into parts; each part is used once for testing while the others train the model. |
| Fold | one part of the cross-validation split | Here the training data are cut into 5 folds (parts). |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| pytest | Python testing tool | Runs the automated checks that prove the data rules hold. |
| D1-D11 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |