Step 12 Report

Transcribe the standards' decision tables

Environment: Claude Code (this chat)   |   Completed: 10 October 2026   |   Report version 2 (11 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The decision tables of the conventional methods were collected online from legitimate sources only (official free previews of the standard and open-access papers). The IEC ratio table and the IEC typical-value table were read directly from the standard (primary source). The Duval Triangle 1 zones come from two agreeing secondary sources and passed every check, but still need a final check against the standard. The Rogers table was transcribed from IEEE Std C57.104-2008 itself (added 11 October 2026); it showed that both secondary Rogers tables contained an error. The copy of that standard was supplied by the researcher and is not licensed to the researcher, so its values must be confirmed against a licensed copy before submission.

# 1. Purpose of this step

The conventional methods (IEC ratio method, Duval Triangle 1 and Rogers ratios) are fixed rule tables written in standards. Before any code uses them, every limit must be copied exactly, with the document, table and page it came from, and checked a second time. The code in later steps will read these files instead of typing numbers by hand.

# 2. Method used

## Approach

Document analysis with double-entry transcription: the decision tables were copied from the primary source where one was available (official previews of IEC 60599) and typed a second time, independently, into a checking program that compares both entries automatically.

Edition tracing: the official lists of technical changes of the 2015 and 2022 editions were used to judge whether the 2007 tables are still current.

Triangulation: each table was compared with independent secondary sources. Where they disagreed (Rogers), neither was used; the conflict was resolved from the standard itself (IEEE Std C57.104-2008, Table 6).

Validation of the Duval zones: the rules were tested on a fine grid covering the whole triangle (every point must fall in exactly one zone), and on every worked example whose diagnosis is printed in a published paper.

## Why this method

•  Copying numbers by hand is error-prone; entering them twice and comparing automatically is a standard way to catch transcription errors.

•  Using the standard itself (primary source) is required for publication; secondary sources are only accepted with agreement checks and a TO VERIFY mark.

•  The grid test proves that the zone rules have no gaps or overlaps, and the worked examples prove they reproduce published diagnoses.

## Settings and rules

| Setting | Value |
| --- | --- |
| Grid for the Duval test | 0.1 % steps - 501 501 points |
| Zone limits | lower limit included (>=), upper limit excluded (<); PD checked first |
| Worked examples | 40 (Duval: Aciu et al. 3, Manisha et al. 36; Rogers: IEEE C57.104-2008 Figure 2); blank gas = 0 ppm (D8) |
| Rogers ratios | R1 = CH4/H2, R2 = C2H2/C2H4, R5 = C2H4/C2H6; printed ranges without stated end points taken as inclusive for the check (the final rule is fixed in Step 14) |
| Second entry | every value typed again in step12_check_tables.py |

## Equations

%CH4=100⋅CH4CH4+C2H4+C2H2#1

where:

CH4, C2H4, C2H2  –  concentrations of methane, ethylene and acetylene [ppm]

%C2H4 and %C2H2 are calculated the same way; the three percentages add up to 100 and fix one point in the Duval Triangle 1.

## Tools and programs

•  06_Python_ML/src/standards/step12_check_tables.py (numpy 2.5.3, pandas 3.0.6)

## Method references

[ST1] IEC 60599:1999+A1:2007, Mineral oil-impregnated electrical equipment in service - Guide to the interpretation of dissolved and free gases analysis, Ed. 2.1. Geneva: IEC, 2007. https://standards.iteh.ai/catalog/standards/iec/31551405-c771-4a06-b021-4c2433c11fb9/iec-60599-1999

[ST2] IEC 60599:1999/AMD1:2007, Amendment 1. Geneva: IEC, 2007. https://standards.iteh.ai/catalog/standards/iec/b3dc8a79-0328-4b58-abec-e6c7a5934dad/iec-60599-1999-amd1-2007

[ST3] IEC 60599:2015 RLV, Mineral oil-filled electrical equipment in service - Guidance on the interpretation of dissolved and free gases analysis, Ed. 3.0. Geneva: IEC, 2015. https://standards.iteh.ai/catalog/standards/iec/645a78c3-5574-4e70-9b7f-4fc4f4abde96/iec-60599-2015

[ST5] IEEE Guide for the Interpretation of Gases Generated in Oil-Immersed Transformers, IEEE Std C57.104-2008 (Revision of IEEE Std C57.104-1991). New York: IEEE, published 2 Feb. 2009. https://standards.ieee.org/ieee/C57.104/4030/ [TO VERIFY against a licensed copy. The 2019 edition (Duval Triangle 1, clause 6.2.3) is still not obtained]

[P1] A. Rangel Bessa, J. Farias Fardin, P. Marques Ciarelli and L. Frizera Encarnacao, "Conventional Dissolved Gases Analysis in Power Transformers: Review," Energies, vol. 16, art. 7219, 2023. doi: 10.3390/en16217219

[P2] A.-M. Aciu, C.-I. Nicola, M. Nicola and M.-C. Nitu, "Complementary Analysis for DGA Based on Duval Methods and Furan Compounds Using Artificial Neural Networks," Energies, vol. 14, art. 588, 2021. doi: 10.3390/en14030588

[P3] Manisha, K. Kaur, N. K. Sharma, J. Singh and D. Bhalla, "Performance Assessment of IEEE/IEC Method and Duval Triangle technique for Transformer Incipient Fault Diagnosis," IOP Conf. Ser.: Mater. Sci. Eng., vol. 1228, art. 012027, 2022. doi: 10.1088/1757-899X/1228/1/012027

[P4] A. Moser, "The Duval Triangle for Transformer Fault Diagnosis," HV Assets, 20 May 2025 (updated 20 July 2025). https://www.hvassets.com/en/post/the-duval-triangle-for-transformer-fault-diagnosis

# 3. Where the tables came from

You asked me to go online and get the standards. Only legitimate copies were used: official free previews published by the standards distributor iTeh, and open-access (Creative Commons) papers. Pirated copies of the standards that appeared in the searches were not opened. No full standard is stored in the project.

| Source | Type | What it gave us |
| --- | --- | --- |
| IEC 60599:1999+A1:2007 (Edition 2.1), official preview | Primary | Table 2 - the IEC ratio table (page 11); Table 3 - simplified scheme (page 12) |
| IEC 60599:1999 Amendment 1:2007, official preview | Primary | Table A.2 - 90 % typical gas values in power transformers |
| IEC 60599:2015 (Edition 3.0) redline, official preview | Primary | Official list of what changed in 2015; table of contents with page numbers |
| IEC 60599:2022 (Edition 4.0), IEC page and preview | Primary | Current edition; what changed in 2022 (clauses A.3 and A.5 only) |
| IEEE Std C57.104-2008 - copy supplied by the researcher (added 11 Oct 2026) | Primary (copy not licensed to the researcher) | Table 6 - Rogers ratios (p.16); Table 1 - Condition 1 limits (p.10); worked example (Figure 2, p.7) |
| Rangel Bessa et al. 2023, Energies (CC BY) | Secondary | Same IEC table (agreement check); one Rogers table |
| Aciu et al. 2021, Energies (CC BY) | Secondary | Same IEC table (agreement check); another Rogers table; 3 worked Duval examples |
| Moser 2025, HV Assets article (cites IEEE C57.104-2019) | Secondary | Duval Triangle 1 zone limits as a table |
| Manisha et al. 2022, IOP conference paper (CC BY 3.0) | Secondary | Duval Triangle 1 figure with zone labels; 35 worked Duval examples |

# 4. What was done, step by step

1.  Searched for the standards and opened only official previews and open-access papers.

2.  Read the official preview of IEC 60599 Edition 2.1 (2007). It shows the full IEC ratio table (Table 2), its notes and the simplified scheme. These values were copied into 02_Standards/iec_ratio_table.csv, one row per fault and ratio, with the text exactly as printed.

3.  Read the official preview of Amendment 1 (2007). It shows Table A.2, the typical gas values used to decide whether a transformer is 'normal'. Copied into 02_Standards/iec_typical_values.csv.

4.  Checked whether these tables changed later. The official 2015 preview lists every significant technical change since 2007; the ratio table (clause 5.4) and the typical values (A.2.4) are not on that list. The 2022 edition changed only clauses A.3 and A.5. So the 2007 values are expected to be the current ones; this is marked TO VERIFY until someone reads the full 2022 text.

5.  Compared the IEC table with two independent open-access papers: both print exactly the same values.

6.  No primary copy of the Duval Triangle 1 limits could be obtained free. Two secondary sources were found that agree: a table citing IEEE C57.104-2019, and the labels on a triangle figure in an open-access paper. The ten zone rules were copied into 02_Standards/duval_triangle_zones.csv and marked SECONDARY - TO VERIFY.

7.  Collected 39 worked Duval examples whose diagnosis is printed in the papers, into 02_Standards/worked_examples.csv. They will become automatic tests for the MATLAB and Python code.

8.  Copied the two Rogers tables found in open-access papers and compared them: they disagree. On 11 October 2026 the researcher supplied a copy of IEEE Std C57.104-2008; its Table 6 (Rogers ratios) and Table 1 (Condition 1 limits) were transcribed into 02_Standards/rogers_ratio_table.csv and ieee_condition1_limits.csv, and the standard's own worked example was added to worked_examples.csv. The two secondary versions were kept, marked superseded, in rogers_secondary_versions.csv.

9.  Second, independent check: a program (06_Python_ML/src/standards/step12_check_tables.py) holds every value typed a second time and compares it with the files, and tests the Duval rules. The record is in 02_Standards/transcription_check.md.

# 5. What we found

## IEC ratio table (IEC 60599, Table 2 of Edition 2.1 = Table 1 of later editions)

| Fault | C2H2/C2H4 | CH4/H2 | C2H4/C2H6 |
| --- | --- | --- | --- |
| PD - partial discharges | NS | < 0.1 | < 0.2 |
| D1 - discharges of low energy | > 1 | 0.1 - 0.5 | > 1 |
| D2 - discharges of high energy | 0.6 - 2.5 | 0.1 - 1 | > 2 |
| T1 - thermal fault below 300 °C | NS | > 1 but NS | < 1 |
| T2 - thermal fault 300-700 °C | < 0.1 | > 1 | 1 - 4 |
| T3 - thermal fault above 700 °C | < 0.2 | > 1 | > 4 |

NS means 'not significant, whatever the value'. The standard says the ratios should be calculated only when at least one gas is above its typical value, and that D1 and D2 overlap, so some cases get a dual D1/D2 answer. Ranges such as 0.1 - 0.5 are printed without saying whether the end points are included; this will be fixed as a written implementation rule in Step 14.

## Typical values (IEC 60599 Amendment 1:2007, Table A.2), in ppm

| Gas | H2 | CH4 | C2H4 | C2H6 | C2H2 (no OLTC) | C2H2 (OLTC) |
| --- | --- | --- | --- | --- | --- | --- |
| 90 % typical range | 50-150 | 30-130 | 60-280 | 20-90 | 2-20 | 60-280 |

These are not limit values. The standard says that when they are exceeded the only recommended action is to test more often. They will be used only as the 'normal or not' gate before the ratio methods, as planned.

## Duval Triangle 1 zones (percent of CH4 + C2H4 + C2H2)

| Zone | Rule (checked in this order) |
| --- | --- |
| PD | CH4 at least 98 % |
| T1 | C2H4 below 20 % and C2H2 below 4 % |
| T2 | C2H4 from 20 to below 50 % and C2H2 below 4 % |
| T3 | C2H4 at least 50 % and C2H2 below 15 % |
| DT | three parts: C2H4 below 50 % with C2H2 4-13 %; C2H4 40-50 % with C2H2 13-29 %; C2H4 at least 50 % with C2H2 15-29 % |
| D1 | C2H4 below 23 % and C2H2 at least 13 % |
| D2 | two parts: C2H4 at least 23 % with C2H2 at least 29 %; C2H4 23-40 % with C2H2 13-29 % |

## Rogers ratios (IEEE Std C57.104-2008, Table 6, page 16)

| Case | C2H2/C2H4 (R2) | CH4/H2 (R1) | C2H4/C2H6 (R5) | Suggested fault diagnosis |
| --- | --- | --- | --- | --- |
| 0 | < 0.1 | > 0.1 to < 1.0 | < 1.0 | Unit normal |
| 1 | < 0.1 | < 0.1 | < 1.0 | Low-energy density arcing - PD |
| 2 | 0.1 to 3.0 | 0.1 to 1.0 | > 3.0 | Arcing - high-energy discharge |
| 3 | < 0.1 | > 0.1 to < 1.0 | 1.0 to 3.0 | Low temperature thermal |
| 4 | < 0.1 | > 1.0 | 1.0 to 3.0 | Thermal < 700 °C |
| 5 | < 0.1 | > 1.0 | > 3.0 | Thermal > 700 °C |

The standard says the Rogers method should be used only when the normal limits of the individual gases (Condition 1 of its Table 1: H2 100, CH4 120, C2H2 1, C2H4 50, C2H6 65 ppm) have been exceeded, and that some ratio combinations fit no case (no diagnosis).

# 6. The Rogers conflict and how it was resolved

The two open-access papers printed different Rogers tables. For arcing, one gave C2H2/C2H4 between 1 and 3, the other between 0.1 and 3.0. For the two lower-temperature thermal faults, one gave C2H4/C2H6 between 1 and 3, the other between 0.1 and 3.

The standard itself (IEEE Std C57.104-2008, Table 6) shows that each paper got one thing wrong: the arcing range is 0.1 to 3.0 (as in Aciu et al.), and the thermal range is 1.0 to 3.0 (as in Rangel Bessa et al.). This is a useful finding for the thesis: copying limits from secondary papers can introduce errors, which is why this project transcribes them from the standard.

Important: the copy of the standard was supplied by the researcher; it is stamped as sold to another organisation and 'Not for Resale', so it is not a copy licensed to the researcher. It was used only to read the limits (facts, cited to the standard), and it is not stored in the project. Before the thesis is submitted, the values must be confirmed against a licensed copy (UMaT library or IEEE Xplore). Decision D10 is closed with this condition.

# 7. Checks

| Check | Result |
| --- | --- |
| IEC ratio table: file vs second entry | 21 of 21 agree - PASS |
| IEC typical values: file vs second entry | 8 of 8 agree - PASS |
| Duval rules: file vs second entry | 10 of 10 agree - PASS |
| Duval rules cover the whole triangle (501 501 test points, 0.1 % steps) | 0 gaps, 0 overlaps - PASS |
| Duval rules reproduce the diagnoses printed in the papers | 39 of 39 - PASS |
| Gas values of the 35 paper examples found in our own IEC TC 10 file | 35 of 35 - PASS |
| Rogers table and Condition 1 limits: file vs second entry | 26 of 26 agree - PASS |
| Rogers rules reproduce the standard's own worked example (Case 2) | 1 of 1 - PASS |

The last two checks give extra confidence in the secondary Duval limits: three independent works (two papers and our own transcription of the IEC TC 10 data) all fit together without a single disagreement.

# 8. Problems and fixes

•  The full IEC 60599:2022 and IEEE C57.104 texts are not free (IEC sells 60599:2022 for CHF 260). Some official previews were tried; the 2007 preview happened to include the ratio table, which solved the most important item.

•  One paper describes zone T2 as 'thermal faults above 700 °C'. This is a wording error in that paper (T2 is 300-700 °C); the zone name it reports is correct and is what we test.

•  One publisher's page asked for a bot check; it was not bypassed and that source was not used.

•  IEEE Std C57.104 is sold only by purchase or subscription, so it could not be obtained free online. The copy later supplied by the researcher turned out to be licensed to another organisation; its limits were used (with that fact recorded) and the file was kept out of the project.

•  While building the earlier step reports, Word froze when saving. The cause was found (the save command must not be called from inside a helper function) and fixed; all reports for Steps 1 and 4-11 were then produced.

# 9. Decisions

•  D10 (recorded in decisions_log.md): IEC tables from the primary 2007 previews, used as current values and marked TO VERIFY against the 2022 text; Duval Triangle 1 from agreeing secondary sources, usable and marked TO VERIFY; Rogers kept (researcher's choice) and transcribed from IEEE Std C57.104-2008 on 11 October 2026 - closed, with the condition that the values are confirmed against a licensed copy before submission.

# 10. Files produced

•  02_Standards: iec_ratio_table.csv, iec_typical_values.csv, duval_triangle_zones.csv, rogers_ratio_table.csv, ieee_condition1_limits.csv, rogers_secondary_versions.csv, worked_examples.csv, transcription_check.md, sources.md

•  06_Python_ML/src/standards/step12_check_tables.py (the checking program)

# 11. What you can do to close the open items

1.  Ask the UMaT library or Prof. Annan for access to IEEE Xplore standards (IEEE C57.104-2008 and 2019) and to IEC 60599:2022, to confirm the transcribed values from licensed copies.

2.  Do not share the IEEE file found in Downloads; it is licensed to another organisation.

# 12. What was achieved

•  The IEC ratio table and the typical-value table were taken from the standard itself (official previews) and checked a second time.

•  The Duval Triangle 1 zones were taken from two agreeing secondary sources and passed every check (no gaps or overlaps; 39 of 39 printed diagnoses reproduced).

•  39 worked examples with printed diagnoses were collected for use as automatic tests.

•  The Rogers conflict was found and documented; on 11 October 2026 the Rogers table was transcribed from IEEE Std C57.104-2008 itself, which showed that both secondary versions contained an error (decision D10 closed, values to be confirmed against a licensed copy).

# 13. Record of this step

| Item | Record |
| --- | --- |
| Step | 12 - Transcribe the standards' decision tables |
| Environment | Claude Code (this chat) |
| Completed | 10 October 2026; Rogers added 11 October 2026 |
| Status | Done - all three methods have their tables (some values TO VERIFY) |
| Main inputs | Official iTeh previews of IEC 60599 (2007, 2015, 2022); open-access papers listed in 02_Standards/sources.md |
| Main outputs | 02_Standards: iec_ratio_table.csv, iec_typical_values.csv, duval_triangle_zones.csv, rogers_ratio_table.csv, ieee_condition1_limits.csv, rogers_secondary_versions.csv, worked_examples.csv (40), transcription_check.md, sources.md |
| Checks | 8 of 8 checks PASS (second entries, triangle coverage, worked examples, data match) |
| Decisions | D10 - Rogers kept and transcribed from IEEE C57.104-2008 (closed with TO VERIFY) |

# 14. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| ST1 | IEC 60599:1999+A1:2007, Mineral oil-impregnated electrical equipment in service - Guide to the interpretation of dissolved and free gases analysis, Ed. 2.1. Geneva: IEC, 2007. Use: Primary source of the IEC ratio table (Table 2, p.11) and simplified scheme (Table 3, p.12); fault definitions (5.2). | https://standards.iteh.ai/catalog/standards/iec/31551405-c771-4a06-b021-4c2433c11fb9/iec-60599-1999; File: 02_Standards/iec_ratio_table.csv |
| ST2 | IEC 60599:1999/AMD1:2007, Amendment 1. Geneva: IEC, 2007. Use: Primary source of Table A.2 (90 % typical gas values in power transformers). | https://standards.iteh.ai/catalog/standards/iec/b3dc8a79-0328-4b58-abec-e6c7a5934dad/iec-60599-1999-amd1-2007; File: 02_Standards/iec_typical_values.csv |
| ST3 | IEC 60599:2015 RLV, Mineral oil-filled electrical equipment in service - Guidance on the interpretation of dissolved and free gases analysis, Ed. 3.0. Geneva: IEC, 2015. Use: List of technical changes 2007 -> 2015 (clause 5.4 and A.2.4 not changed); page numbers of Table 1, Table A.2 and Figure B.3. | https://standards.iteh.ai/catalog/standards/iec/645a78c3-5574-4e70-9b7f-4fc4f4abde96/iec-60599-2015; File: 02_Standards/sources.md |
| ST4 | IEC 60599:2022, Mineral oil-filled electrical equipment in service - Guidance on the interpretation of dissolved and free gases analysis, Ed. 4.0. Geneva: IEC, 2022. Use: Current edition; changes vs 2015 only in A.3 and A.5. Full text needed to confirm the transcribed tables (TO VERIFY). | https://webstore.iec.ch (search 'IEC 60599:2022'); preview: https://cdn.standards.iteh.ai/samples/104040/d30f5b4c122043798470a8b63c4b273a/IEC-60599-2022.pdf |
| ST5 | IEEE Guide for the Interpretation of Gases Generated in Oil-Immersed Transformers, IEEE Std C57.104-2008 (Revision of IEEE Std C57.104-1991). New York: IEEE, published 2 Feb. 2009. Use: Rogers ratio table (Table 6, p.16); Condition 1 limits (Table 1, p.10); Rogers worked example (Figure 2, p.7). | https://standards.ieee.org/ieee/C57.104/4030/; File: 02_Standards/rogers_ratio_table.csv; 02_Standards/ieee_condition1_limits.csv |
| P1 | A. Rangel Bessa, J. Farias Fardin, P. Marques Ciarelli and L. Frizera Encarnacao, "Conventional Dissolved Gases Analysis in Power Transformers: Review," Energies, vol. 16, art. 7219, 2023. Use: Agreement check of the IEC table (Table 6); Rogers version A (Table 4). | https://doi.org/10.3390/en16217219; DOI 10.3390/en16217219; File: 02_Standards/iec_ratio_table.csv; rogers_ratio_table.csv |
| P2 | A.-M. Aciu, C.-I. Nicola, M. Nicola and M.-C. Nitu, "Complementary Analysis for DGA Based on Duval Methods and Furan Compounds Using Artificial Neural Networks," Energies, vol. 14, art. 588, 2021. Use: Agreement check of the IEC table (Table 4); Rogers version B (Table 3); 3 worked Duval examples (Tables 12, 14, 16). | https://doi.org/10.3390/en14030588; DOI 10.3390/en14030588; File: 02_Standards/rogers_ratio_table.csv; worked_examples.csv |
| P3 | Manisha, K. Kaur, N. K. Sharma, J. Singh and D. Bhalla, "Performance Assessment of IEEE/IEC Method and Duval Triangle technique for Transformer Incipient Fault Diagnosis," IOP Conf. Ser.: Mater. Sci. Eng., vol. 1228, art. 012027, 2022. Use: Duval Triangle 1 boundary labels (Figure 2); 35 worked Duval examples (Tables 4 and 6). | https://doi.org/10.1088/1757-899X/1228/1/012027; DOI 10.1088/1757-899X/1228/1/012027; File: 02_Standards/duval_triangle_zones.csv; worked_examples.csv |
| P4 | A. Moser, "The Duval Triangle for Transformer Fault Diagnosis," HV Assets, 20 May 2025 (updated 20 July 2025). Use: Duval Triangle 1 zone limits as a table (Table 1; cites IEEE C57.104-2019 clause 6.2.3). | https://www.hvassets.com/en/post/the-duval-triangle-for-transformer-fault-diagnosis; File: 02_Standards/duval_triangle_zones.csv |
| P5 | J. Dukarm, Z. Draper and T. Piotrowski, "Diagnostic Simplexes for Dissolved-Gas Analysis," Energies, vol. 13, art. 6459, 2020. Use: Consulted for Duval zone limits; contains none - nothing taken. | https://doi.org/10.3390/en13236459; DOI 10.3390/en13236459 |
| DS1 | M. Duval and A. dePablo, "Interpretation of gas-in-oil analysis using new IEC publication 60599 and IEC TC 10 databases," IEEE Electrical Insulation Magazine, vol. 17, no. 2, pp. 31-41, Mar./Apr. 2001. Use: Main benchmark (labels confirmed by inspection): primary analysis = 58 power transformers (codes P, U); sensitivity = all 117. | https://doi.org/10.1109/57.917529; DOI 10.1109/57.917529; File: 03_Data/raw/iec_tc10_duval2001_full/iec_tc10_faulty_equipment.csv; SHA-256 EF9F6B542821264A... |
| DF5 | Made in Step 12 from ST1-ST4 and P1-P4. Use: Limits used by the conventional methods (Steps 14-17). | File: 02_Standards/*.csv |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 15. How this helps the next steps

Next step: Step 13: freeze data version 1.0 - record the fingerprints (hashes) of the processed data, these standards tables and plot_style.csv, so that every later result can be traced to exactly these files.

•  In Steps 14-17 the MATLAB Agentic Toolkit implements the IEC ratio method, Duval Triangle 1 and Rogers by reading these files - no limit is typed by hand.

•  worked_examples.csv becomes a set of automatic tests, so the MATLAB code can be shown to give the same answers as the published sources.

•  iec_typical_values.csv provides the limits for the normality gate (decision D3).

•  Step 13 records the fingerprints of these files, so every later result can be traced to exactly these tables.

# 16. Open items and limitations

•  Rogers table and Condition 1 limits: read from a copy of IEEE C57.104-2008 that is not licensed to the researcher - confirm against a licensed copy before submission.

•  Duval Triangle 1 zones: to be confirmed against IEEE C57.104-2019 clause 6.2.3 or IEC 60599:2022 Figure B.3.

•  IEC tables: to be confirmed against the full IEC 60599:2022 text.

•  Whether the end points of ranges such as 0.1 - 0.5 are included is not stated in the standard; this will be fixed as a written rule in Step 14.

# 17. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| CH4 | methane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H6 | ethane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H4 | ethylene | Hydrocarbon gas favoured above about 500 °C; it rises as thermal faults get hotter. |
| C2H2 | acetylene | Gas that needs at least 800 to 1 200 °C; formed in significant amounts mainly in electrical arcs. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| D2 | discharges of high energy | Arcing with power follow-through: extensive carbonisation, metal fusion, sometimes tripping of the equipment. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| T2 | thermal fault 300 to 700 °C | Overheating in which the paper has carbonised. |
| T3 | thermal fault above 700 °C | Very hot fault: carbonised oil, metal colouring (800 °C) or metal fusion (above 1 000 °C). |
| DT | mixture of thermal and electrical faults | A zone of the Duval Triangle 1 for cases that look partly thermal and partly electrical. |
| NS | non-significant | In the IEC ratio table: this ratio is not used for that fault, whatever its value. |
| OLTC | on-load tap changer | A switch that changes the transformer's voltage ratio while it is in service; its sparking makes gases that can leak into the main tank. |
| LV, HV | low voltage, high voltage | The lower- and higher-voltage sides (windings, connections) of a transformer. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| IEEE | Institute of Electrical and Electronics Engineers | A professional body that publishes engineering standards and journals. |
| IEEE C57.104 | IEEE guide for the interpretation of gases generated in oil-immersed transformers | The IEEE standard that contains the Duval Triangle 1 (2019 edition) and the Rogers ratio table (2008 edition). |
| iTeh | iTeh Standards | A standards distributor that publishes official free previews of standards. |
| CC BY | Creative Commons Attribution licence | An open-access licence: the paper may be read and reused freely if the authors are credited. |
| Ratio method | diagnosis from gas ratios | Divides one gas by another (for example C2H2/C2H4) and compares the result with fixed limits to name the fault. |
| Duval Triangle 1 | graphical DGA method by M. Duval | The shares of CH4, C2H4 and C2H2 are plotted as one point in a triangle divided into fault zones. |
| Rogers ratios | older gas-ratio method by R.R. Rogers | A ratio table that names faults from three gas ratios; kept in IEEE C57.104. |
| Typical values | 90 % typical gas concentrations | Levels below which about 90 % of transformers in service are found; not limit values. |
| Normality gate | rule that lets conventional methods answer 'Normal' | If all gases are below their typical values, the conventional methods give Normal instead of a fault (decision D3). |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| D1-D11 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Primary and secondary source | the original document and a document that quotes it | Values from a secondary source are marked TO VERIFY until checked against the primary source. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| R1, R2, R5 | Rogers gas ratios | R1 = CH4/H2, R2 = C2H2/C2H4, R5 = C2H4/C2H6; the three ratios the Rogers method compares with its table. |
| Condition 1 | IEEE normal-level gas limits | The highest gas levels at which IEEE C57.104 considers a transformer to be operating satisfactorily (e.g. H2 100 ppm, C2H2 1 ppm). |