Step 14 Report

Complete the conventional-method functions

Environment: MATLAB (run from Claude Code through the MATLAB MCP connection)   |   Completed: 11 October 2026   |   Report version 1 (11 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The IEC 60599 ratio method, the Rogers ratio method and Duval Triangle 1 are now complete MATLAB functions. Every decision limit is read from the frozen tables in 02_Standards; an automatic audit found no limit typed in the code. Before the code was trusted, the written rules were run on all 827 records. They exposed three gaps - 99 records have a zero denominator, 27 records would match both PD and T1, and the Duval boundary distance was ambiguous - which the researcher settled as decision D12 before any result was produced. A further point found in Step 16 (IEC could then never answer PD alone) was settled as decision D13 (T1 requires CH4/H2 > 1), and Steps 14 to 17 were run again. The normality gate and the boundary distances of the Analysis Plan (Equations 9 and 10) are implemented.

# 1. Purpose of this step

The conventional methods are the yardstick against which machine learning is judged. This step turns the three methods into reliable, annotated functions that give one answer for one sample or for thousands, that never contain a hand-typed limit, and that also measure how close each sample lies to a line where the diagnosis would change (needed to test the boundary hypothesis, research question RQ2).

# 2. Method used

## Approach

Table-driven programming: the MATLAB code contains no decision limit. A loader (load_standards) reads the limits from the frozen CSV files in 02_Standards, and the diagnosis functions only interpret those tables. Changing a limit therefore means changing a CSV file and creating a new data version, never editing code.

Three methods, two engines. The IEC 60599 ratio method and the Rogers ratio method use one ratio-table engine: a class matches when every ratio the table uses for that class is defined and lies inside its interval; no match gives ND (no diagnosis); several matches are returned together (only D1/D2 occurs). Duval Triangle 1 applies its 10 rules in order and the first match wins.

Normality gate: a sample is called Normal when every gas is at or below the upper end of its IEC 60599 typical-value range (the lower end is kept as a sensitivity). The same gate is used for all three methods; the method's own answer is kept separately as the raw result.

Distance to the nearest decision boundary: for the ratio methods, in decades of the ratio (Analysis Plan Eq. 9); for the Duval Triangle, in percentage points to the nearest edge that separates two different zones (Eq. 10 with decision D12). The Duval zones are first turned into polygons (polygon clipping), and the edges between different zones are found by looking a tiny distance to each side of every polygon edge.

Audit: a program lists every numeric literal left in the decision code (comments and text removed) and fails if any is not on a short list of bookkeeping numbers.

## Why this method

•  Reading limits from the standards tables keeps one source of truth, so the MATLAB and the later Python implementation (Step 18) can be compared on the same limits, and every limit can be traced to a clause and page.

•  One shared engine for the IEC and Rogers tables means both methods obey exactly the same rules for strict and inclusive limits and for undefined ratios, which is required for a fair comparison.

•  Keeping the raw result next to the gated result lets the thesis report the conventional methods with and without the normality gate, and lets the unit tests check the methods against published examples that were never gated.

•  A decision-boundary distance that ignores the triangle sides and the seams inside one zone measures what the boundary hypothesis (RQ2) is about: how close a sample is to a line where the diagnosis would change.

•  An automatic audit is more reliable than reading the code by eye: it makes the rule 'no limit typed in code' testable.

## Settings and rules

| Setting | Value |
| --- | --- |
| Data version | 1.0, checked at the start of every program (16 files, SHA-256) |
| Gas columns | H2, CH4, C2H6, C2H4, C2H2 in ppm; not detected = 0 ppm (decision D8) |
| Ratios | R1 = CH4/H2, R2 = C2H2/C2H4, R5 = C2H4/C2H6; a zero denominator makes the ratio undefined (NaN) |
| Interval rules (D11) | < and > strict; printed ranges 'a - b' include both end points; 'NS' (not significant) entries are not used |
| Undefined ratio (D12) | ND only when a ratio the class uses is undefined; an undefined NS ratio does not stop a class from matching |
| Several IEC classes match | joined with '/': only D1/D2 occurs (D11); PD/T1 was removed by D13 |
| T1 condition (D13) | the printed 'CH4/H2 > 1 but NS' is used as R1 > 1 (strict), so PD (R1 < 0.1) and T1 never overlap |
| Rogers cases to classes (D11) | 0 Normal, 1 PD, 2 D2, 3 T1, 4 T2, 5 T3 (Rogers has no D1 case) |
| Duval rules (D11) | applied in rule_order, first match wins; lower limit inclusive (>=), upper limit exclusive (<); DT is a valid zone |
| Normality gate (D11) | upper end of IEC Table A.2 (primary), lower end (sensitivity); C2H2 uses the communicating-OLTC range only for equipment code U |
| Boundary distance (Eq. 9, Eq. 10, D12) | ratio methods: decades, a ratio of 0 gives Inf; Duval: percentage points in a triangle of side 100, decision edges only |
| Numerical constants in code | 100 (percentages add up to 100) and 1e-6 percentage points (probe offset); both in conv_config.m |

## Equations

R1=CH4H2#1

where:

R1  –  first ratio (dimensionless)

CH4  –  methane concentration [ppm]

H2  –  hydrogen concentration [ppm]

R2 = C2H2/C2H4 and R5 = C2H4/C2H6 are calculated in the same way (acetylene/ethylene and ethylene/ethane). A zero denominator makes the ratio undefined.

pX=100⋅XCH4+C2H4+C2H2#2

where:

pX  –  percentage of gas X in the three-gas total [%]

X  –  concentration of one of the gases CH4, C2H4 or C2H2 [ppm]

The three percentages add up to 100 and fix one point in Duval Triangle 1 (Analysis Plan Eq. 4).

x=pC2H4+pCH42#3

where:

x  –  horizontal position of the sample in the triangle [percentage points]

pC2H4, pCH4  –  percentages of ethylene and methane [%]

The vertical position is y = (√3/2)·p(CH4). In this plane the side of the triangle is 100 units long, so one unit is one percentage point along a side.

dR=minj,llog10Rj-log10Lj,l#4

where:

dR  –  distance of the sample to the nearest ratio limit [decades]

j  –  index of the ratio (R1, R2 or R5)

l  –  index of a limit of ratio j in the code table

Rj  –  value of ratio j for the sample (dimensionless)

Lj,l  –  limit l of ratio j read from 02_Standards (dimensionless)

dD=mine∈EdistP,e#5

where:

dD  –  distance of the sample to the nearest decision edge [percentage points]

P  –  the sample point in the plane of the triangle

E  –  the set of edges that separate two different zones (decision D12)

distP,e  –  shortest distance from P to the segment e [percentage points]

## Tools and programs

•  MATLAB R2025b (25.2.0.2998904), base MATLAB only. Program files in 04_MATLAB_Conventional: conv_config, verify_data_version, load_standards, gas_ratios, duval_xy, bound_test, diagnose_ratio_method, diagnose_duval, normality_gate, boundary_distance_ratio, duval_zone_polygons, duval_decision_edges, boundary_distance_duval, conventional_diagnosis, run_conventional_batch, check_no_typed_limits, impact_of_rules.

•  Code Analyzer (checkcode) run on every file; SHA-256 through java.security.MessageDigest; readtable with explicit column types.

## Method references

[ST1] IEC 60599:1999+A1:2007, Mineral oil-impregnated electrical equipment in service - Guide to the interpretation of dissolved and free gases analysis, Ed. 2.1. Geneva: IEC, 2007. https://standards.iteh.ai/catalog/standards/iec/31551405-c771-4a06-b021-4c2433c11fb9/iec-60599-1999

[ST2] IEC 60599:1999/AMD1:2007, Amendment 1. Geneva: IEC, 2007. https://standards.iteh.ai/catalog/standards/iec/b3dc8a79-0328-4b58-abec-e6c7a5934dad/iec-60599-1999-amd1-2007

[ST5] IEEE Guide for the Interpretation of Gases Generated in Oil-Immersed Transformers, IEEE Std C57.104-2008 (Revision of IEEE Std C57.104-1991). New York: IEEE, published 2 Feb. 2009. https://standards.ieee.org/ieee/C57.104/4030/ [TO VERIFY against a licensed copy. The 2019 edition (Duval Triangle 1, clause 6.2.3) is still not obtained]

[P3] Manisha, K. Kaur, N. K. Sharma, J. Singh and D. Bhalla, "Performance Assessment of IEEE/IEC Method and Duval Triangle technique for Transformer Incipient Fault Diagnosis," IOP Conf. Ser.: Mater. Sci. Eng., vol. 1228, art. 012027, 2022. doi: 10.1088/1757-899X/1228/1/012027

[P4] A. Moser, "The Duval Triangle for Transformer Fault Diagnosis," HV Assets, 20 May 2025 (updated 20 July 2025). https://www.hvassets.com/en/post/the-duval-triangle-for-transformer-fault-diagnosis

[M8] I. E. Sutherland and G. W. Hodgman, "Reentrant polygon clipping," Communications of the ACM, vol. 17, no. 1, pp. 32-42, Jan. 1974. https://cacmb4.acm.org/magazines/1974/1/11767-reentrant-polygon-clipping

[M9] IEEE Standard for Floating-Point Arithmetic, IEEE Std 754-2019, 2019. doi: 10.1109/IEEESTD.2019.8766229

# 3. What was used

| Input | Content and source | Status |
| --- | --- | --- |
| 02_Standards/iec_ratio_table.csv | IEC 60599:1999+A1:2007 (Ed. 2.1) Table 2, page 11: 18 rows (6 classes x 3 ratios); the 'simplified scheme' rows (Table 3) are not used. [ST1] | PRIMARY preview; TO VERIFY against the 2022 text |
| 02_Standards/iec_typical_values.csv | IEC 60599 AMD1:2007 Table A.2: typical values of the five gases (normality gate). [ST2] | PRIMARY preview; TO VERIFY for 2015/2022 |
| 02_Standards/rogers_ratio_table.csv | IEEE Std C57.104-2008 Table 6: Rogers cases 0 to 5 (18 rows). [ST5] | TO VERIFY against a licensed copy |
| 02_Standards/duval_triangle_zones.csv | Duval Triangle 1: 10 rules (Moser 2025; Manisha et al. 2022). [P4, P3] | SECONDARY; TO VERIFY |
| 03_Data/processed/dga_master.csv | 827 records, five gases in ppm, data version 1.0. [DF2] | frozen |
| 03_Data/data_version_1.0.sha256 | Fingerprints of the 16 frozen files, checked at the start of every program. [DF6] | frozen |
| Decision D11 and Analysis Plan Section 4.5 | Implementation rules and the definition of the boundary distance (Equations 9 and 10). | approved 11 Oct 2026 |

# 4. Reading the instructions critically before coding

The toolkit instructions were not followed blindly. Before any code was written, the rules of decision D11 were tried on the real data with a short scratch program, and the existing code stubs and the CSV tables were compared. Eight points were found; four needed the researcher's decision and were put to the researcher with a recommendation each (the fourth, on PD and T1, after Step 16).

| Finding | Evidence | Action |
| --- | --- | --- |
| 1. A zero denominator gave ND even when the ratio is not needed | 99 of 827 records have a zero denominator. Example: the first IEC TC 10 record (a partial discharge) has C2H4 = 0 and C2H2 = 0, so R2 = 0/0, although the IEC table marks R2 as not significant for PD and T1. D11 as written gave ND for 239 records; ND only when a needed ratio is undefined gives 204 (figures at the time of decision D12). | Researcher chose: ND only when a ratio that the class uses is undefined (35 records diagnosed instead of ND at that time). Decision D12 (1). |
| 2. PD and T1 can match together | 27 records satisfy both PD and T1 when T1 ignores CH4/H2 (printed NS). D11 only covers D1/D2 (90 records). | Researcher first chose the dual answer PD/T1 (D12 (2)); replaced by D13 after Step 16 (finding 4). |
| 3. Equation 10 read literally counts non-decision lines | 'The nearest zone edge' would include the three sides of the triangle and seams between rules of the same zone (for example the two D2 rules). Crossing them never changes the diagnosis. | Researcher chose: only edges that separate two different zones, distance in percentage points. Decision D12 (3). |
| 4. Consequence of finding 2 | If T1 ignores CH4/H2, PD (R1 < 0.1 and R5 < 0.2) always satisfies T1 (R5 < 1), so IEC could never answer PD alone, only PD/T1. Found in Step 16. | Researcher chose: the printed 'CH4/H2 > 1' of T1 is used as a condition (decision D13). PD and T1 no longer overlap; PD alone now occurs for |
| 5. The old code stubs do not fit the real tables | gas_ratios, conventional_diagnosis and plot_duval_triangle expected a 'wide' ratio table and polygon vertices; the real CSV files are 'long' ratio tables with bound types and a rule table. The README listed other file names. | Rewritten; the old function names and the dashboard calls (d.rogers, d.iec, d.duval, plot_duval_triangle) were kept. |
| 6. Published examples were never gated | Worked examples MAN-22 and MAN-23 print T1, but all their gases are below the normality gate. | The Step 15 tests compare the raw method result, before the gate. |
| 7. Toolkit set-up not finished | The instructions say Steps 2 and 3 (toolkit set-up) must be finished first. They are not. | The MATLAB MCP connection of Claude Code was used. Accepted by the researcher (decision D14). |
| 8. Side effect of decision D13 | Using the printed '> 1' as a condition for T1 raises IEC ND from 204 to 319 records (T1 records with CH4/H2 of 1 or less, or undefined, no longer match). | Reported to the researcher; to be justified in the thesis. |

# 5. What was done, step by step

1.  Read the instructions, the Analysis Plan (Section 4.5), decision D11, the five standards tables and the old code. Tried the D11 rules on all 827 records (see the findings above) and put the three open questions to the researcher; the answers became decision D12. After Step 16 two further questions (PD and T1; the toolkit set-up) were put and answered as decisions D13 and D14, and Steps 14 to 17 were run again.

2.  Wrote conv_config.m (paths, names, the Rogers case mapping, two numerical constants) and verify_data_version.m (SHA-256 of the 16 frozen files with java.security.MessageDigest).

3.  Wrote load_standards.m, which reads the IEC Table 2 rows (18), the Rogers rows (18), the 10 Duval rules and the 8 typical-value rows, with every column read as text or as a number explicitly.

4.  Wrote gas_ratios.m (R1, R2, R5 and the Duval percentages; zero denominator gives NaN), duval_xy.m, bound_test.m (the D11 interval rules), diagnose_ratio_method.m (IEC and Rogers engine), diagnose_duval.m (10 rules, first match wins) and normality_gate.m.

5.  Wrote the Duval geometry: duval_zone_polygons.m turns every rule into a polygon; duval_decision_edges.m keeps the edge pieces with a different zone on each side; boundary_distance_duval.m measures the distance. Checked: the ten polygons have a total area of 5000 (the triangle has 5000), there are 30 decision-edge pieces, and a point at 19.9 % C2H4 lies 0.1 x (sqrt 3)/2 = 0.0866 percentage points from the T1/T2 edge.

6.  Wrote boundary_distance_ratio.m (Equation 9; a ratio of 0 gives Inf, an undefined ratio does not count).

7.  Wrote conventional_diagnosis.m (one call for one or many samples) and run_conventional_batch.m (data-version check, master table, three methods, output files).

8.  Wrote check_no_typed_limits.m and ran it; wrote impact_of_rules.m so that the numbers behind decision D12 are saved files; ran the Code Analyzer on every file.

9.  Added a help text (purpose, inputs, outputs, rules, sources) to every file, and rewrote the README of 04_MATLAB_Conventional.

# 6. The rules as implemented

| Rule | Source | Where in the code |
| --- | --- | --- |
| Limits are read from 02_Standards, never typed | Toolkit instructions, rule 1 | load_standards.m; audit in check_no_typed_limits.m |
| < and > strict; printed ranges include both end points; NS entries not used | D11 rule 3 | bound_test.m; the 'ignored' flag in load_standards.m |
| A class matches only if every ratio it uses is defined and inside its interval; otherwise ND | D11 rule 7 as amended by D12 (1) | diagnose_ratio_method.m |
| Several IEC classes match: answer with all of them (only D1/D2 occurs) | D11 rule 4 | diagnose_ratio_method.m |
| T1 needs CH4/H2 > 1 (the printed '> 1 but NS' is used as a condition) | D13 | load_standards.m; bound_test.m |
| Rogers cases 0 to 5 are Normal, PD, D2, T1, T2, T3 | D11 rule 5 | conv_config.m; load_standards.m |
| Duval rules in rule_order; lower limit inclusive, upper exclusive; DT valid | D11 (Duval rule) | diagnose_duval.m |
| Normality gate: upper end primary, lower end sensitivity; same gate for all methods; C2H2 range by equipment code U | D11 rules 1, 2, 6 | normality_gate.m; conventional_diagnosis.m |
| Ratio boundary distance in decades; Duval distance in percentage points to edges between different zones | Analysis Plan Eq. 9; Eq. 10 with D12 (3) | boundary_distance_ratio.m; duval_decision_edges.m; boundary_distance_duval.m |

# 7. What we found

## Effect of decisions D12 and D13 (saved in impact_of_rules.csv)

| Item | Records |
| --- | --- |
| Records in the master table | 827 |
| Records with at least one zero denominator (R1, R2 or R5) | 99 |
| At the time of D12 (T1 still ignoring CH4/H2): IEC ND if any undefined ratio gives ND (D11 as first written) | 239 |
| At the time of D12: IEC ND if only a ratio the class uses is undefined | 204 |
| At the time of D12: records diagnosed under D12 but ND under D11 as first written | 35 |
| Records that would match both PD and T1 if T1 ignored CH4/H2 | 27 |
| Final rules (D12 and D13): IEC ND, any undefined ratio gives ND | 335 |
| Final rules: IEC ND, only a used ratio undefined (raw, before the gate) | 319 |
| Final rules: records matching both D1 and D2 (dual answer D1/D2) | 90 |
| Final rules: records matching both PD and T1 | 0 |
| Final rules: IEC result PD alone (raw) | 27 |
| Rogers ND before the gate (unchanged by D12 and D13: every Rogers case uses all three ratios) | 424 |

## What the normality gate does (saved in gate_by_class.csv)

| Data role | Records | Called Normal by the upper gate | of which true faults | Called Normal by the lower gate |
| --- | --- | --- | --- | --- |
| Development | 439 | 164 | 92 | 71 |
| Internal test | 70 | 24 | 14 | 8 |
| IEC TC 10 benchmark | 117 | 10 | 10 | 4 |
| External test (Li 2019) | 201 | 44 | 44 | 8 |
| All records | 827 | 242 | 160 | 91 |

The gate is the researcher's approved design (decision D11). It matters: 160 of the 242 records that the upper gate calls Normal are true faults with low gas levels. For those records the three conventional methods are bound to be wrong, whatever their ratios. The lower gate (sensitivity) calls 91 records Normal. IEC 60599 Annex A states that the typical values are 90 % observation ranges and not fault limits; this is recorded as a limitation.

## Geometry of Duval Triangle 1

The ten rules give ten convex polygons with a total area of 5000 in (%C2H4, %C2H2) coordinates, which equals the area of the triangle (100 x 100 / 2): the rules leave no gap and do not overlap. 30 edge pieces separate two different zones; the triangle sides and the seams between rules of the same zone are not counted.

# 8. Checks

| Check | Result |
| --- | --- |
| No decision limit typed in the code (check_no_typed_limits, 17 files audited) | 0 disallowed numeric literals - PASS |
| Data version 1.0 verified at the start of the batch run (16 files) | 0 differences - PASS |
| Duval polygons cover the triangle exactly once | 5000 of 5000 - PASS |
| Hand checks of the Duval boundary distance (points 60 %, 19.9 % and 20 % C2H4 at 1 % C2H2) | 8.66, 0.0866 and 0 percentage points, as calculated by hand - PASS |
| All 827 records processed in one call | about 1.3 s - PASS |
| Code Analyzer on every file | no warning in the decision code; three informational notes reviewed (see Open items) |

# 9. Problems and fixes

•  The first run of the audit reported 27 numeric literals. They were the column numbers of the five gases (4 and 5), the 0.5 of the triangle geometry and cosmetic numbers (axis ranges, font sizes, colours) of the two plotting files. The audit was refined, not the code: the numbers 0 to 5 are allowed as indices, 0.5 only in duval_xy.m, 100 and 1e-6 only in conv_config.m, and plotting files are not audited because they take no part in any decision. The decision code now passes with 0 literals.

•  The first version of the CSV reader failed because a text option was set on numeric columns; the options are now set per column type. MATLAB also warns that the first Rogers column is called 'case', a MATLAB keyword; the column is read by position and the warning is switched off for that read only.

•  The existing stubs could not read the real tables (finding 5). They were replaced, keeping the names used by the dashboard.

•  After Step 16 showed that IEC could never answer PD alone, decision D13 changed the T1 rule. The code (load_standards, bound_test), the tests, the evidence file impact_of_rules.csv (which now keeps the figures of the D12 stage next to the final ones) and every output of Steps 14 to 17 were updated and run again; the figures of this report are from the final run.

# 10. Decisions

•  Decision D12 (researcher, 11 October 2026): (1) ND only when a ratio that the class uses is undefined; (2) dual answer PD/T1 treated like D1/D2 (later replaced by D13); (3) Duval boundary distance = distance to the nearest edge that separates two different zones, in percentage points.

•  Decision D13 (researcher, 11 October 2026, after Step 16): the printed 'CH4/H2 > 1 but NS' of T1 is used as the condition CH4/H2 > 1 (strict). PD and T1 no longer overlap and IEC can answer PD alone. This departs slightly from the printed table; IEC ND rises from 204 to 319 records (raw).

•  Decision D14 (researcher, 11 October 2026): the MATLAB steps may be run through the MATLAB MCP connection; Steps 2-3 are recorded as replaced for MATLAB.

# 11. Files produced

•  04_MATLAB_Conventional: conv_config.m, verify_data_version.m, load_standards.m, gas_ratios.m, duval_xy.m, bound_test.m, diagnose_ratio_method.m, diagnose_duval.m, normality_gate.m, boundary_distance_ratio.m, duval_zone_polygons.m, duval_decision_edges.m, boundary_distance_duval.m, conventional_diagnosis.m, run_conventional_batch.m, check_no_typed_limits.m, impact_of_rules.m, README.md, code_manifest.sha256 (fingerprints of the 22 code files).

•  11_Results/conventional: impact_of_rules.csv, gate_by_class.csv, no_typed_limits_audit.csv.

•  00_Project_Admin/decisions_log.md (D12, D13, D14); data and source register (SW2, M8, M9, DF8, DF11); abbreviations glossary.

# 12. What was achieved

•  The three conventional methods now read every limit from the frozen standards tables; the audit found 0 typed limits in the decision code.

•  Running the written rules on the real data exposed three gaps; they were reported to the researcher and settled as decision D12 before any result was produced. A fourth point found in Step 16 (IEC could never answer PD alone) was settled as decision D13 and Steps 14 to 17 were run again.

•  Boundary distances (Analysis Plan Eq. 9 and Eq. 10) are implemented and tested.

•  A batch function reads the master table after verifying the SHA-256 fingerprints of all 16 frozen files.

# 13. Record of this step

| Item | Record |
| --- | --- |
| Step | 14 - Complete the conventional-method functions |
| Environment | MATLAB, run from Claude Code through the MATLAB MCP connection (toolkit Steps 2-3 not yet checked) |
| Completed | 11 October 2026 |
| Status | Done |
| Main inputs | 02_Standards CSV files, 03_Data/processed/dga_master.csv (data version 1.0), decision D11, Analysis Plan Section 4.5 |
| Main outputs | 20 MATLAB files in 04_MATLAB_Conventional; impact_of_rules.csv and gate_by_class.csv in 11_Results/conventional |
| Checks | no typed limits (audit PASS); Code Analyzer reviewed; data version verified; polygons cover the triangle exactly |
| Decisions | D12 - three amendments found while implementing D11; D13 - T1 requires CH4/H2 > 1; D14 - MATLAB steps through the MCP connection (all closed by the researcher) |

# 14. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| ST1 | IEC 60599:1999+A1:2007, Mineral oil-impregnated electrical equipment in service - Guide to the interpretation of dissolved and free gases analysis, Ed. 2.1. Geneva: IEC, 2007. Use: Primary source of the IEC ratio table (Table 2, p.11) and simplified scheme (Table 3, p.12); fault definitions (5.2). | https://standards.iteh.ai/catalog/standards/iec/31551405-c771-4a06-b021-4c2433c11fb9/iec-60599-1999; File: 02_Standards/iec_ratio_table.csv |
| ST2 | IEC 60599:1999/AMD1:2007, Amendment 1. Geneva: IEC, 2007. Use: Primary source of Table A.2 (90 % typical gas values in power transformers). | https://standards.iteh.ai/catalog/standards/iec/b3dc8a79-0328-4b58-abec-e6c7a5934dad/iec-60599-1999-amd1-2007; File: 02_Standards/iec_typical_values.csv |
| ST5 | IEEE Guide for the Interpretation of Gases Generated in Oil-Immersed Transformers, IEEE Std C57.104-2008 (Revision of IEEE Std C57.104-1991). New York: IEEE, published 2 Feb. 2009. Use: Rogers ratio table (Table 6, p.16); Condition 1 limits (Table 1, p.10); Rogers worked example (Figure 2, p.7). | https://standards.ieee.org/ieee/C57.104/4030/; File: 02_Standards/rogers_ratio_table.csv; 02_Standards/ieee_condition1_limits.csv |
| P3 | Manisha, K. Kaur, N. K. Sharma, J. Singh and D. Bhalla, "Performance Assessment of IEEE/IEC Method and Duval Triangle technique for Transformer Incipient Fault Diagnosis," IOP Conf. Ser.: Mater. Sci. Eng., vol. 1228, art. 012027, 2022. Use: Duval Triangle 1 boundary labels (Figure 2); 35 worked Duval examples (Tables 4 and 6). | https://doi.org/10.1088/1757-899X/1228/1/012027; DOI 10.1088/1757-899X/1228/1/012027; File: 02_Standards/duval_triangle_zones.csv; worked_examples.csv |
| P4 | A. Moser, "The Duval Triangle for Transformer Fault Diagnosis," HV Assets, 20 May 2025 (updated 20 July 2025). Use: Duval Triangle 1 zone limits as a table (Table 1; cites IEEE C57.104-2019 clause 6.2.3). | https://www.hvassets.com/en/post/the-duval-triangle-for-transformer-fault-diagnosis; File: 02_Standards/duval_triangle_zones.csv |
| DF2 | Made in Step 9 from DS1-DS5 (Steps 5-9 programs). Use: All clean records with role, class, flags and original values. | File: 03_Data/processed/dga_master.csv; SHA-256 AE9E6C0C84CF7180... |
| DF5 | Made in Step 12 from ST1-ST4 and P1-P4. Use: Limits used by the conventional methods (Steps 14-17). | File: 02_Standards/*.csv |
| DF6 | Made in Step 13 from all frozen files. Use: SHA-256 of every frozen file; checked by verify_data_version() before every later step. | File: 03_Data/data_version_1.0.sha256; SHA-256 260EBE0C8921E52C... |
| DF8 | Made in Steps 14-17: 22 MATLAB files in 04_MATLAB_Conventional and its tests folder. Use: The three conventional methods, boundary distances, tests, batch run, figures. | File: 04_MATLAB_Conventional/code_manifest.sha256; SHA-256 01055ECB9487CE67... |
| DF11 | Made in Step 14 by impact_of_rules.m (impact_of_rules.csv and gate_by_class.csv). Use: Evidence for decision D12; gate_by_class.csv SHA-256 E249F9B6899420A56958DCDF934F926492B11DFB24553AF628391F37A3D9F51D. | File: 11_Results/conventional/impact_of_rules.csv; SHA-256 11A215384496E2D3... |
| SW2 | MATLAB R2025b, version 25.2.0.2998904, The MathWorks, Inc., Natick, MA, USA. Use: Runs the conventional-method functions, unit tests, batch run and Duval figures (Steps 14-17). | https://www.mathworks.com/products/matlab.html |

# 15. How this helps the next steps

Next step: Step 15 [MATLAB] - unit-test the conventional methods with the 40 published worked examples, the zero-denominator rules, the boundary rules of D11 to D13 and the normality gate, and save the test log.

•  Step 15 tests these functions against the 40 published worked examples and the D11/D12 boundary rules.

•  Step 16 runs run_conventional_batch on all 827 records.

•  Step 17 draws the Duval Triangle from duval_zone_polygons and duval_decision_edges.

•  Step 18 re-implements the methods in Python from the same tables and compares the two outputs record by record.

# 16. Open items and limitations

•  The IEC and Rogers tables and the Duval limits are still TO VERIFY against primary sources (IEC 60599:2022, a licensed IEEE C57.104).

•  Decision D13 uses the printed 'CH4/H2 > 1 but NS' of T1 as a condition. This departs slightly from the printed table (which marks the entry NS) and raises IEC ND from 204 to 319 of 827 records (raw). It should be justified in the thesis.

•  The normality gate is the researcher's approved design; IEC 60599 Annex A says typical values are not fault limits. 160 of the 242 gated records are true faults (see the findings).

•  Steps 2 and 3 (toolkit set-up) were not done; the MATLAB MCP connection of Claude Code was used instead. The researcher accepted this for MATLAB (decision D14); the Simulink toolkit set-up is still to be decided before Stage G.

•  Code Analyzer messages that were reviewed and left: the unused compatibility argument zoneFile in plot_duval_triangle, an axes call inside a loop in plot_duval_by_role, and notes in the test files about variable names that equal property names.

# 17. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| CH4 | methane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H6 | ethane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H4 | ethylene | Hydrocarbon gas favoured above about 500 °C; it rises as thermal faults get hotter. |
| C2H2 | acetylene | Gas that needs at least 800 to 1 200 °C; formed in significant amounts mainly in electrical arcs. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| D2 | discharges of high energy | Arcing with power follow-through: extensive carbonisation, metal fusion, sometimes tripping of the equipment. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| T2 | thermal fault 300 to 700 °C | Overheating in which the paper has carbonised. |
| T3 | thermal fault above 700 °C | Very hot fault: carbonised oil, metal colouring (800 °C) or metal fusion (above 1 000 °C). |
| DT | mixture of thermal and electrical faults | A zone of the Duval Triangle 1 for cases that look partly thermal and partly electrical. |
| NS | non-significant | In the IEC ratio table: this ratio is not used for that fault, whatever its value. |
| OLTC | on-load tap changer | A switch that changes the transformer's voltage ratio while it is in service; its sparking makes gases that can leak into the main tank. |
| P, U, R, I, B, C, S | equipment codes of the IEC TC 10 database | P power transformer without, U with a communicating OLTC; R reactor; I instrument transformer; B bushing; C cable; S tap-changer selector compartment. |
| LV, HV | low voltage, high voltage | The lower- and higher-voltage sides (windings, connections) of a transformer. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| IEEE | Institute of Electrical and Electronics Engineers | A professional body that publishes engineering standards and journals. |
| IEEE C57.104 | IEEE guide for the interpretation of gases generated in oil-immersed transformers | The IEEE standard that contains the Duval Triangle 1 (2019 edition) and the Rogers ratio table (2008 edition). |
| Ratio method | diagnosis from gas ratios | Divides one gas by another (for example C2H2/C2H4) and compares the result with fixed limits to name the fault. |
| Duval Triangle 1 | graphical DGA method by M. Duval | The shares of CH4, C2H4 and C2H2 are plotted as one point in a triangle divided into fault zones. |
| Rogers ratios | older gas-ratio method by R.R. Rogers | A ratio table that names faults from three gas ratios; kept in IEEE C57.104. |
| Typical values | 90 % typical gas concentrations | Levels below which about 90 % of transformers in service are found; not limit values. |
| Normality gate | rule that lets conventional methods answer 'Normal' | If all gases are below their typical values, the conventional methods give Normal instead of a fault (decision D3). |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Not detected | gas below the laboratory's detection limit | Treated as 0 ppm in this thesis (decision D8). |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| Simulink, Simscape | MATLAB's block-diagram modelling tool and its physical-modelling library | Used to model the transformer's operating conditions (Simulink Agentic Toolkit); it never makes gas values. |
| D1-D14 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| R1, R2, R5 | Rogers gas ratios | R1 = CH4/H2, R2 = C2H2/C2H4, R5 = C2H4/C2H6; the three ratios the Rogers method compares with its table. |
| Condition 1 | IEEE normal-level gas limits | The highest gas levels at which IEEE C57.104 considers a transformer to be operating satisfactorily (e.g. H2 100 ppm, C2H2 1 ppm). |
| ND (no diagnosis) | No diagnosis | The answer of a method when no rule applies or a ratio it needs cannot be calculated. It is a result and is never deleted. |
| Dual answer (D1/D2) | Two classes returned together | Sometimes the IEC table fits two fault types at once. The method then answers with both (D1/D2); it counts as correct if the true class is either one. |
| Boundary distance | Distance to the nearest decision boundary | How far a sample is from the line where the diagnosis would change. A small distance means a small measurement error could change the diagnosis. |
| Decade (log10 unit) | A factor of 10 | A distance of 1 decade on the ratio scale means the ratio is 10 times larger or smaller, e.g. from 0.1 to 1. |
| Rogers case | Rogers diagnosis code 0 to 5 | The Rogers table gives each combination of ratios a case number: 0 normal, 1 partial discharge, 2 arcing, 3 and 4 thermal below 700 degrees, 5 thermal above 700 degrees. |
| Raw and final result | Result before and after the normality gate | raw_result is what the method itself says; result is what is left after samples with low gas levels have been called Normal by the gate. |
| Polygon clipping (Sutherland-Hodgman) | Cutting a shape with straight lines | A standard way to find the area of the triangle that satisfies one limit after another; used to draw the Duval zones from their limits. |
| Unit test (matlab.unittest) | Automatic test of one small piece of code | A test that feeds a function a known input and checks the answer, so that any later change that breaks the function is noticed at once. |