Step 15 Report

Unit-test the conventional methods

Environment: MATLAB (run from Claude Code through the MATLAB MCP connection)   |   Completed: 11 October 2026   |   Report version 1 (11 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: A test class with 67 automatic tests was written and run. All 67 pass. They reproduce all 39 Duval Triangle 1 worked examples and the Rogers worked example of IEEE Std C57.104-2008, and they fix in code the rules of decisions D11 to D13 for zero denominators, for samples exactly on a limit and for the normality gate. The log of the run is saved. One test failed on the way because the author had written a wrong expected value; the code was right.

# 1. Purpose of this step

A method that has not been tested against known answers cannot be trusted in a thesis. This step shows that the MATLAB functions of Step 14 give the published answers, that the rules agreed with the researcher are applied exactly, and that the code stays correct when it is changed later.

# 2. Method used

## Approach

Unit testing with the MATLAB testing framework (matlab.unittest): each test gives a function a known input and checks the answer. The tests are written as one class, and one command runs all of them and writes a log.

Reference examples: every row of worked_examples.csv is one test - 39 Duval Triangle 1 examples printed in two open-access papers and 1 Rogers example printed in IEEE Std C57.104-2008 (Figure 2). The method's own answer, before the normality gate, must equal the printed diagnosis.

Boundary construction: for the boundary tests the gas values are chosen so that a ratio or a percentage is exactly equal to a limit (for example CH4/H2 = 0.1), and the answer is compared with the rule of decision D11.

Structure tests: the Duval polygons must cover the triangle exactly once; no two Rogers cases may match the same sample; the only IEC overlap allowed is D1/D2; both are checked on dense grids that include every printed limit.

## Why this method

•  Reproducing published, independently calculated examples shows that the implementation does what the sources say, which is the accepted way to validate a re-implementation of a standard.

•  Boundary cases are where implementations differ (strict or inclusive limits); testing them exactly makes the choice explicit and permanent.

•  A test log that records the MATLAB version and every test is evidence that can be shown to supervisors and examiners, and the tests catch accidental changes in later steps.

## Settings and rules

| Setting | Value |
| --- | --- |
| Test class | 04_MATLAB_Conventional/tests/TestConventionalMethods.m |
| Number of tests | 67 (41 worked-example tests, 6 zero-denominator, 7 boundary, 3 gate, 10 structure) |
| What is compared for the examples | raw method result (before the normality gate) against the printed diagnosis |
| Blank gas in an example | 0 ppm (decision D8: not detected) |
| Rogers example tolerance | ratios compared with the printed 0.29, 0.70 and 4.25 within 0.005 |
| Command | run_tests_and_log (calls runtests; writes tests/test_log.txt; raises an error if any test fails) |

## Tools and programs

•  MATLAB R2025b matlab.unittest (runtests, TestCase, parameterised tests, verifyEqual, verifyTrue, verifyError)

•  04_MATLAB_Conventional/tests/run_tests_and_log.m

## Method references

[P2] A.-M. Aciu, C.-I. Nicola, M. Nicola and M.-C. Nitu, "Complementary Analysis for DGA Based on Duval Methods and Furan Compounds Using Artificial Neural Networks," Energies, vol. 14, art. 588, 2021. doi: 10.3390/en14030588

[P3] Manisha, K. Kaur, N. K. Sharma, J. Singh and D. Bhalla, "Performance Assessment of IEEE/IEC Method and Duval Triangle technique for Transformer Incipient Fault Diagnosis," IOP Conf. Ser.: Mater. Sci. Eng., vol. 1228, art. 012027, 2022. doi: 10.1088/1757-899X/1228/1/012027

[ST5] IEEE Guide for the Interpretation of Gases Generated in Oil-Immersed Transformers, IEEE Std C57.104-2008 (Revision of IEEE Std C57.104-1991). New York: IEEE, published 2 Feb. 2009. https://standards.ieee.org/ieee/C57.104/4030/ [TO VERIFY against a licensed copy. The 2019 edition (Duval Triangle 1, clause 6.2.3) is still not obtained]

[M9] IEEE Standard for Floating-Point Arithmetic, IEEE Std 754-2019, 2019. doi: 10.1109/IEEESTD.2019.8766229

# 3. What was used

| Input | Content |
| --- | --- |
| 04_MATLAB_Conventional functions | The functions written in Step 14 (data version 1.0 standards tables). |
| 02_Standards/worked_examples.csv | 40 worked examples: 3 from Aciu et al. 2021 and 36 from Manisha et al. 2022 (all 39 for Duval Triangle 1), and 1 Rogers example from IEEE Std C57.104-2008 Figure 2. Blank gas = 0 ppm. [P2, P3, ST5] |
| Decisions D11 to D13 | The boundary, zero-denominator and T1 rules the tests must enforce. |

# 4. What was done, step by step

1.  Wrote TestConventionalMethods.m as a matlab.unittest class. The 40 worked examples are loaded from worked_examples.csv and each becomes one test (a parameterised test), so adding an example to the CSV adds a test.

2.  Wrote the zero-denominator tests (undefined ratio, zero numerator, Rogers and IEC with a needed ratio undefined, the D12 case of an undefined NS ratio, Duval with all three gases at 0 ppm).

3.  Built boundary samples whose ratio or percentage equals a limit exactly, and wrote the expected answer from the rule of D11/D12 for each (table below).

4.  Wrote the gate tests: upper end, lower end, the tap-changer rule for C2H2, one common gate for the three methods. The limits used to build the samples are read from iec_typical_values.csv, not typed.

5.  Wrote the structure tests: polygons cover the triangle once; every grid point has a Duval zone; no two Rogers cases overlap (dense logarithmic grid that includes every printed limit and values just above and below); the only IEC overlap is D1/D2; boundary-distance values; data version; batch size; no typed limits.

6.  Wrote run_tests_and_log.m, which runs the class with runtests and writes tests/test_log.txt (date, MATLAB version, full output, one line per test) and stops with an error if any test fails.

7.  Ran the tests, found and settled the problems described below, and ran them again until all passed.

# 5. What the tests check

| Group | Tests | What is checked |
| --- | --- | --- |
| (a) Worked examples | 41 | 40 tests, one per row of worked_examples.csv (39 Duval Triangle 1, 1 Rogers), plus a test that the file really has 39 + 1 rows. The raw method result is compared with the printed diagnosis. |
| (b) Zero denominators | 6 | Undefined ratio is NaN; zero numerator is a valid 0; Rogers and IEC give ND when a needed ratio is undefined; an undefined NS ratio still lets PD match (D12); Duval gives ND when CH4 = C2H4 = C2H2 = 0. |
| (c) Samples on a limit | 7 | Strict < and > ; printed ranges include both end points; Duval lower limit inclusive, upper exclusive; T1 needs CH4/H2 > 1 (D13); the interval function itself. |
| (d) Normality gate | 3 | Upper end, lower end, C2H2 range by equipment code U, one gate for all methods. |
| (e) Structure | 10 | Polygon coverage; every point has a zone; Rogers cases never overlap; the only IEC overlap is D1/D2; ratio and Duval boundary distances; triangle sides and seams not counted; data version; batch size; no typed limits. |

# 6. What we found

## Result of the run

The saved log (tests/test_log.txt) ends with: SUMMARY: 67 tests, 67 passed, 0 failed, 0 incomplete.

## The worked examples

| Method | Printed diagnosis | Number of examples (all reproduced) |
| --- | --- | --- |
| Duval Triangle 1 | D1 | 6 |
| Duval Triangle 1 | D2 | 16 |
| Duval Triangle 1 | PD | 1 |
| Duval Triangle 1 | T1 | 4 |
| Duval Triangle 1 | T2 | 5 |
| Duval Triangle 1 | T3 | 7 |
| Rogers ratios | Case 2 - possible arcing | 1 |

All 39 Duval Triangle 1 examples and the Rogers example give exactly the printed diagnosis. For the Rogers example the ratios R2 = 5/17, R1 = 190/270 and R5 = 17/4 also agree with the printed 0.29, 0.70 and 4.25 and the case is Case 2 (mapped to D2).

## Boundary samples tested (decisions D11 to D13)

| Sample (gases in ppm) | What it tests | Expected and obtained |
| --- | --- | --- |
| H2 100, CH4 10, C2H6 100, C2H4 1, C2H2 0 (R1 = 0.1) | PD needs R1 < 0.1 (strict); T1 needs R1 > 1 (D13) | IEC: ND |
| H2 10000, CH4 999, C2H6 100, C2H4 1, C2H2 0 (R1 = 0.0999) | just below the limit | IEC: PD only |
| H2 10, CH4 20, C2H6 10, C2H4 5, C2H2 0 (R1 = 2, R5 = 0.5); and the same with CH4 10 (R1 = 1) | T1 needs CH4/H2 > 1 (strict), decision D13 | IEC: T1; with R1 = 1: ND |
| H2 10, CH4 5, C2H6 2, C2H4 10, C2H2 20 (R1 = 0.5) | printed range 0.1 - 0.5 includes 0.5 | IEC: D1/D2 |
| H2 100, CH4 10, same other gases (R1 = 0.1) | printed range includes 0.1 | IEC: D1/D2 |
| H2 100, CH4 9.99, same other gases (R1 = 0.0999) | just below 0.1 | IEC: ND |
| H2 10, CH4 20, C2H6 10, C2H4 40, C2H2 0 (R5 = 4) | T2 range 1 - 4 includes 4; T3 needs R5 > 4 | IEC: T2 only |
| same with C2H4 41 (R5 = 4.1) | just above 4 | IEC: T3 |
| H2 10, CH4 10, C2H6 5, C2H4 10, C2H2 0.5 (R1 = 1, R2 = 0.05, R5 = 2) | Rogers: cases 0 and 3 need R1 < 1, cases 4 and 5 need R1 > 1 | Rogers: ND |
| H2 10, CH4 10, C2H6 5, C2H4 20, C2H2 10 (R1 = 1, R2 = 0.5, R5 = 4) | Case 2 prints R1 as 0.1 to 1.0 (included) | Rogers: Case 2 = D2 |
| CH4 79, C2H4 20, C2H2 1 (%C2H4 = 20) | Duval lower limit included | Duval: T2 |
| CH4 79.5, C2H4 19.5, C2H2 1 (%C2H4 = 19.5) | just below 20 | Duval: T1 |
| CH4 49, C2H4 50, C2H2 1 (%C2H4 = 50) | T2 needs < 50 (upper excluded) | Duval: T3 |
| CH4 98, C2H4 1, C2H2 1 (%CH4 = 98) | PD needs >= 98 | Duval: PD |
| CH4 76, C2H4 20, C2H2 4 (%C2H2 = 4) | T zones need %C2H2 < 4 | Duval: DT |

Each of these samples is built so that the ratio or percentage is exactly equal to the limit. Because a division in IEEE 754 arithmetic is correctly rounded, a quotient that is exactly equal to a printed limit (for example 3/30 and 0.1) gives exactly the number of the limit, so the strict and inclusive rules decide the boundary case as intended [M9].

# 7. Checks

| Check | Result |
| --- | --- |
| runtests on TestConventionalMethods | 67 tests, 67 passed, 0 failed, 0 incomplete |
| All 40 worked examples reproduced | 40 of 40 - PASS |
| Polygon area equals the triangle area | 5000 of 5000 - PASS |
| Test log saved with date and MATLAB version | 04_MATLAB_Conventional/tests/test_log.txt |

# 8. Problems and fixes

•  The first run could not create the test suite: the parameters of the worked-example tests are built before the class setup puts the code folder on the path. The parameter function now adds the folder to the path itself.

•  One test failed: the distance from the point (35 %, 0 %) to the nearest Duval decision edge. The author had expected 15 x (sqrt 3)/2, forgetting the T2/DT limit at %C2H2 = 4. A hand calculation gives 4 x (sqrt 3)/2 = 3.464, which is what the code returned. The expected value in the test was wrong, not the code, and was corrected.

•  After the sanity-check program of Step 16 was added, the 'no typed limits' test failed once because that program contained the number 7 (the number of columns of a table). The program was changed to count its columns; the audit was not loosened. The log in the project is from the final run: 67 of 67 pass.

•  Decision D13 (T1 requires CH4/H2 > 1) changed the expected answers of three tests (PD/T1 became PD or ND), turned the overlap test into a test of the single overlap D1/D2, and added one test for the T1 rule (66 tests became 67). The log in the project is from the run after these changes.

# 9. Decisions

•  None new. The tests enforce decisions D11, D12 and D13.

# 10. Files produced

•  04_MATLAB_Conventional/tests: TestConventionalMethods.m, run_tests_and_log.m, test_log.txt, README.md.

# 11. What was achieved

•  67 automatic tests were written; all 67 pass on the final code (log saved).

•  All 39 Duval Triangle 1 worked examples and the Rogers example from IEEE C57.104-2008 are reproduced exactly.

•  The boundary rules of decision D11 and the amendments of D12 and D13 are fixed by tests.

•  One failing test was traced to a wrong expected value written by the author, not to the code; the expected value was corrected after a hand calculation.

# 12. Record of this step

| Item | Record |
| --- | --- |
| Step | 15 - Unit-test the conventional methods |
| Environment | MATLAB, run from Claude Code through the MATLAB MCP connection |
| Completed | 11 October 2026 |
| Status | Done - 67 of 67 tests pass |
| Main inputs | 04_MATLAB_Conventional functions; 02_Standards/worked_examples.csv |
| Main outputs | tests/TestConventionalMethods.m, tests/run_tests_and_log.m, tests/test_log.txt, tests/README.md |
| Checks | runtests 67 passed, 0 failed, 0 incomplete |
| Decisions | none new |

# 13. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| ST5 | IEEE Guide for the Interpretation of Gases Generated in Oil-Immersed Transformers, IEEE Std C57.104-2008 (Revision of IEEE Std C57.104-1991). New York: IEEE, published 2 Feb. 2009. Use: Rogers ratio table (Table 6, p.16); Condition 1 limits (Table 1, p.10); Rogers worked example (Figure 2, p.7). | https://standards.ieee.org/ieee/C57.104/4030/; File: 02_Standards/rogers_ratio_table.csv; 02_Standards/ieee_condition1_limits.csv |
| P2 | A.-M. Aciu, C.-I. Nicola, M. Nicola and M.-C. Nitu, "Complementary Analysis for DGA Based on Duval Methods and Furan Compounds Using Artificial Neural Networks," Energies, vol. 14, art. 588, 2021. Use: Agreement check of the IEC table (Table 4); Rogers version B (Table 3); 3 worked Duval examples (Tables 12, 14, 16). | https://doi.org/10.3390/en14030588; DOI 10.3390/en14030588; File: 02_Standards/rogers_ratio_table.csv; worked_examples.csv |
| P3 | Manisha, K. Kaur, N. K. Sharma, J. Singh and D. Bhalla, "Performance Assessment of IEEE/IEC Method and Duval Triangle technique for Transformer Incipient Fault Diagnosis," IOP Conf. Ser.: Mater. Sci. Eng., vol. 1228, art. 012027, 2022. Use: Duval Triangle 1 boundary labels (Figure 2); 35 worked Duval examples (Tables 4 and 6). | https://doi.org/10.1088/1757-899X/1228/1/012027; DOI 10.1088/1757-899X/1228/1/012027; File: 02_Standards/duval_triangle_zones.csv; worked_examples.csv |
| DF5 | Made in Step 12 from ST1-ST4 and P1-P4. Use: Limits used by the conventional methods (Steps 14-17). | File: 02_Standards/*.csv |
| DF8 | Made in Steps 14-17: 22 MATLAB files in 04_MATLAB_Conventional and its tests folder. Use: The three conventional methods, boundary distances, tests, batch run, figures. | File: 04_MATLAB_Conventional/code_manifest.sha256; SHA-256 01055ECB9487CE67... |
| DF13 | Made in Step 15 by run_tests_and_log.m (66 tests). Use: Proof that the MATLAB code reproduces the published worked examples and the D11/D12 rules. | File: 04_MATLAB_Conventional/tests/test_log.txt; SHA-256 165D3B7CF93C2A3E... |
| SW2 | MATLAB R2025b, version 25.2.0.2998904, The MathWorks, Inc., Natick, MA, USA. Use: Runs the conventional-method functions, unit tests, batch run and Duval figures (Steps 14-17). | https://www.mathworks.com/products/matlab.html |

# 14. How this helps the next steps

Next step: Step 16 [MATLAB] - run the three methods on all 827 records and write conventional_predictions.csv with one row per record and method; report the number of ND, DT and dual results per method and data role.

•  Step 16 can now run the three methods on all records with confidence that they reproduce published diagnoses.

•  Any later change to a function or to a standards table is checked by running run_tests_and_log again.

•  Step 18 compares the Python re-implementation with the same 40 examples and with the MATLAB output.

# 15. Open items and limitations

•  The worked examples come from papers (secondary sources) and one standard. Reproducing them shows the implementation matches those sources; it does not prove that the limits themselves are correct (TO VERIFY items remain).

•  There is only one Rogers example; the other Rogers cases are checked by boundary tests and the no-overlap test, not by published examples.

•  The Duval limits were first checked in Step 12 with Python (39 of 39); this step repeats the check in MATLAB. The two are not yet independent of each other because they use the same CSV file.

# 16. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| CH4 | methane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H6 | ethane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H4 | ethylene | Hydrocarbon gas favoured above about 500 °C; it rises as thermal faults get hotter. |
| C2H2 | acetylene | Gas that needs at least 800 to 1 200 °C; formed in significant amounts mainly in electrical arcs. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| D2 | discharges of high energy | Arcing with power follow-through: extensive carbonisation, metal fusion, sometimes tripping of the equipment. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| T2 | thermal fault 300 to 700 °C | Overheating in which the paper has carbonised. |
| T3 | thermal fault above 700 °C | Very hot fault: carbonised oil, metal colouring (800 °C) or metal fusion (above 1 000 °C). |
| DT | mixture of thermal and electrical faults | A zone of the Duval Triangle 1 for cases that look partly thermal and partly electrical. |
| NS | non-significant | In the IEC ratio table: this ratio is not used for that fault, whatever its value. |
| OLTC | on-load tap changer | A switch that changes the transformer's voltage ratio while it is in service; its sparking makes gases that can leak into the main tank. |
| P, U, R, I, B, C, S | equipment codes of the IEC TC 10 database | P power transformer without, U with a communicating OLTC; R reactor; I instrument transformer; B bushing; C cable; S tap-changer selector compartment. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEEE | Institute of Electrical and Electronics Engineers | A professional body that publishes engineering standards and journals. |
| IEEE C57.104 | IEEE guide for the interpretation of gases generated in oil-immersed transformers | The IEEE standard that contains the Duval Triangle 1 (2019 edition) and the Rogers ratio table (2008 edition). |
| Ratio method | diagnosis from gas ratios | Divides one gas by another (for example C2H2/C2H4) and compares the result with fixed limits to name the fault. |
| Duval Triangle 1 | graphical DGA method by M. Duval | The shares of CH4, C2H4 and C2H2 are plotted as one point in a triangle divided into fault zones. |
| Rogers ratios | older gas-ratio method by R.R. Rogers | A ratio table that names faults from three gas ratios; kept in IEEE C57.104. |
| Typical values | 90 % typical gas concentrations | Levels below which about 90 % of transformers in service are found; not limit values. |
| Normality gate | rule that lets conventional methods answer 'Normal' | If all gases are below their typical values, the conventional methods give Normal instead of a fault (decision D3). |
| Not detected | gas below the laboratory's detection limit | Treated as 0 ppm in this thesis (decision D8). |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Log scale | logarithmic axis | Each step on the axis is ten times the previous one, so very small and very large values fit on one chart. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| D1-D14 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Primary and secondary source | the original document and a document that quotes it | Values from a secondary source are marked TO VERIFY until checked against the primary source. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| R1, R2, R5 | Rogers gas ratios | R1 = CH4/H2, R2 = C2H2/C2H4, R5 = C2H4/C2H6; the three ratios the Rogers method compares with its table. |
| Condition 1 | IEEE normal-level gas limits | The highest gas levels at which IEEE C57.104 considers a transformer to be operating satisfactorily (e.g. H2 100 ppm, C2H2 1 ppm). |
| ND (no diagnosis) | No diagnosis | The answer of a method when no rule applies or a ratio it needs cannot be calculated. It is a result and is never deleted. |
| Dual answer (D1/D2) | Two classes returned together | Sometimes the IEC table fits two fault types at once. The method then answers with both (D1/D2); it counts as correct if the true class is either one. |
| Boundary distance | Distance to the nearest decision boundary | How far a sample is from the line where the diagnosis would change. A small distance means a small measurement error could change the diagnosis. |
| Rogers case | Rogers diagnosis code 0 to 5 | The Rogers table gives each combination of ratios a case number: 0 normal, 1 partial discharge, 2 arcing, 3 and 4 thermal below 700 degrees, 5 thermal above 700 degrees. |
| Polygon clipping (Sutherland-Hodgman) | Cutting a shape with straight lines | A standard way to find the area of the triangle that satisfies one limit after another; used to draw the Duval zones from their limits. |
| Unit test (matlab.unittest) | Automatic test of one small piece of code | A test that feeds a function a known input and checks the answer, so that any later change that breaks the function is noticed at once. |
| IEEE 754 | Floating-point arithmetic standard | The rule that decides how computers round decimal numbers; it makes a division that is exactly equal to a limit give exactly the limit. |