Step 16 Report

Run the three methods on every record

Environment: MATLAB (run from Claude Code through the MATLAB MCP connection)   |   Completed: 11 October 2026   |   Report version 1 (11 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The three methods were applied to all 827 records of data version 1.0; the file conventional_predictions.csv has 2481 rows (one per record and method) and keeps every ND, DT and dual answer. After the upper normality gate, 242 records are called Normal. The remaining results contain ND for 200 records (IEC), 296 (Rogers) and 1 (Duval). These counts are descriptive; nothing is concluded yet about which method is better.

# 1. Purpose of this step

This step produces the conventional answers that every later comparison needs: agreement with the Python re-implementation (Step 18), comparison with machine learning, the tests of disagreement, and the boundary-distance analysis. It also reports how often each method gives no diagnosis, a Duval DT or a dual IEC answer.

# 2. Method used

## Approach

Batch application: after the data-version check, the three methods are applied to every record of the master table in one vectorised call, and the result is written as one row per record and method.

Both answers are kept: raw_result is the method's own answer and result is the answer after the upper normality gate. ND, DT and dual answers are results and stay in the file; nothing is removed or filled in.

Counting: the numbers of ND, DT, D1/D2 (and PD/T1, now always 0) results are counted per method and data role, after and before the gate.

Plausibility check: the raw answers are compared with the inspection-confirmed class of the IEC TC 10 benchmark, on the five merged classes. This only shows that the implementations behave sensibly; the formal evaluation comes later.

Read-back: the output file is read again in a different program (Python) to check its size, record order and columns.

## Why this method

•  A single, versioned prediction file is the input of every later comparison (agreement with Python, with machine learning, McNemar tests, boundary-distance regression), so it must contain everything those analyses need.

•  Keeping ND and dual answers makes the unresolved share of each method visible instead of hiding it; reviewers of DGA studies ask for this.

•  A plausibility check against known classes catches gross mistakes (for example a swapped ratio) before they spread into later steps; it is deliberately not reported as a result.

## Settings and rules

| Setting | Value |
| --- | --- |
| Records | 827 (all data roles of data version 1.0) |
| Rows written | 827 x 3 methods = 2481, in record order: IEC60599, Rogers, Duval |
| Gate columns | gate_upper and gate_lower: 'Normal' or blank |
| Boundary distance column | decades (IEC, Rogers) or percentage points (Duval); Inf if every defined ratio is 0; NaN if undefined |
| Plausibility scoring (not a result) | classes PD, D1, D2, T12, T3; T1 and T2 count as T12; a dual answer is correct if either part is correct; DT and ND count as wrong; raw answers |
| Output folder | 11_Results/conventional |

## Tools and programs

•  04_MATLAB_Conventional/run_conventional_batch.m, sanity_check_vs_truth.m, impact_of_rules.m

•  Python 3.12.10 with pandas (read-back check, python -I)

# 3. What was used

| Input | Content |
| --- | --- |
| 03_Data/processed/dga_master.csv | 827 records: development 439, internal test 70, IEC TC 10 benchmark 117, external test 201. [DF2] |
| 04_MATLAB_Conventional | The functions of Step 14, tested in Step 15 (code fingerprints in code_manifest.sha256). [DF8] |
| 02_Standards | The frozen limit tables. [DF5] |

# 4. What was done, step by step

1.  Ran run_conventional_batch, which first verified the SHA-256 fingerprints of all 16 frozen files (0 differences), read the master table and called conventional_diagnosis on all records at once (about 1.3 s).

2.  Built the output with one row per record and method, in record order (IEC60599, Rogers, Duval), with the gate columns, raw_result, result, the ratios or Duval percentages, the boundary distance and the data version.

3.  Counted the results per method and data role, before and after the gate, and saved the counts.

4.  Read the file again in Python (pandas) to confirm 2481 rows, 827 unique records in master-table order, the columns, and that the result equals Normal exactly where the upper gate is passed and equals raw_result elsewhere.

5.  Ran the plausibility check against the IEC TC 10 benchmark (see below) and the impact check of Step 14, and wrote the README of 11_Results/conventional.

# 5. What we found

## Results of the three methods on all 827 records (after the upper normality gate)

| Result | IEC 60599 ratio | Rogers ratio | Duval Triangle 1 |
| --- | --- | --- | --- |
| Normal | 242 | 263 | 242 |
| PD | 23 | 13 | 41 |
| D1 | 63 | 0 | 138 |
| D2 | 36 | 126 | 158 |
| T1 | 55 | 8 | 45 |
| T2 | 48 | 34 | 66 |
| T3 | 77 | 87 | 114 |
| D1/D2 | 83 | 0 | 0 |
| PD/T1 | 0 | 0 | 0 |
| DT | 0 | 0 | 22 |
| ND | 200 | 296 | 1 |
| Total | 827 | 827 | 827 |

Reading the table: a zero means that the method never gives that answer. Rogers has no D1 case (a limitation of the table); the PD/T1 row is 0 since decision D13; DT is a Duval zone only. IEC ND is high (T1 now needs CH4/H2 > 1).

## ND, DT and dual answers per method and data role

| Method | Data role | n | Normal by gate | ND | DT | D1/D2 | PD/T1 | ND before gate |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| IEC60599 | all | 827 | 242 | 200 | 0 | 83 | 0 | 319 |
| IEC60599 | development | 439 | 164 | 115 | 0 | 23 | 0 | 192 |
| IEC60599 | internal_test | 70 | 24 | 19 | 0 | 5 | 0 | 36 |
| IEC60599 | benchmark | 117 | 10 | 24 | 0 | 25 | 0 | 27 |
| IEC60599 | external_test | 201 | 44 | 42 | 0 | 30 | 0 | 64 |
| Rogers | all | 827 | 242 | 296 | 0 | 0 | 0 | 424 |
| Rogers | development | 439 | 164 | 157 | 0 | 0 | 0 | 250 |
| Rogers | internal_test | 70 | 24 | 28 | 0 | 0 | 0 | 35 |
| Rogers | benchmark | 117 | 10 | 42 | 0 | 0 | 0 | 47 |
| Rogers | external_test | 201 | 44 | 69 | 0 | 0 | 0 | 92 |
| Duval | all | 827 | 242 | 1 | 22 | 0 | 0 | 2 |
| Duval | development | 439 | 164 | 1 | 15 | 0 | 0 | 2 |
| Duval | internal_test | 70 | 24 | 0 | 4 | 0 | 0 | 0 |
| Duval | benchmark | 117 | 10 | 0 | 1 | 0 | 0 | 0 |
| Duval | external_test | 201 | 44 | 0 | 2 | 0 | 0 | 0 |

ND, DT and the dual answers are counted after the upper gate (a gated record is Normal, so it is not counted); the last column gives ND before the gate. The complete table, including the same counts before the gate, is in conventional_counts.csv.

## What the gate does to the true faults

The upper gate calls 242 records Normal; 160 of them are true faults (gate_by_class.csv). The lower gate calls 91 records Normal. Because the same gate is used for all three methods, these records are counted as Normal for every method; the raw_result column keeps what each method alone would have said.

## Plausibility check against the IEC TC 10 benchmark (not a result)

| Method | Records | Correct | Share | ND | DT | Dual answers |
| --- | --- | --- | --- | --- | --- | --- |
| IEC60599 | 117 | 81 | 69.2% | 27 | 0 | 27 |
| Rogers | 117 | 55 | 47.0% | 47 | 0 | 0 |
| Duval | 117 | 103 | 88.0% | 0 | 1 | 0 |

This check uses the raw answers (before the gate) on the 117 inspection-confirmed benchmark records with the classes merged to PD, D1, D2, T12 and T3; a dual answer counts as correct if either part is right, and DT and ND count as wrong. It only shows that the three implementations behave sensibly: the Duval triangle is clearly the most accurate on this data set, the IEC ratio method is intermediate with many dual and ND answers, and the Rogers method leaves many records without diagnosis. The formal evaluation (macro-F1, confidence intervals, the primary 58-record subset, the gate, the scoring of dual answers) is done in later steps and may give different figures. Nothing here should be quoted as a result.

# 6. Checks

| Check | Result |
| --- | --- |
| Rows in conventional_predictions.csv | 2481 = 827 x 3 - PASS |
| Unique records and order | 827; same order as dga_master.csv - PASS |
| ND rows kept | yes: IEC 200, Rogers 296, Duval 1 - PASS |
| result equals Normal where the upper gate is passed, raw_result elsewhere | all 2481 rows - PASS (checked in Python) |
| Data version 1.0 verified before the run | 16 files, 0 differences - PASS |
| Audit of typed limits after adding the new programs | 0 disallowed literals - PASS |

# 7. Problems and fixes

•  The first version of the plausibility program contained the number 7 for the number of table columns; the audit test flagged it (see Step 15). The program was changed, and all programs and figures were run again, so that every saved file comes from the final code.

•  Undefined ratios and distances are stored as NaN and infinite distances as Inf (the file has 14 Inf and 4 NaN boundary distances); Python reads both correctly.

# 8. Decisions

•  None new. Decisions D8, D11, D12 and D13 were applied.

# 9. Files produced

•  11_Results/conventional: conventional_predictions.csv, conventional_counts.csv, sanity_agreement_benchmark.csv, impact_of_rules.csv, gate_by_class.csv, README.md.

•  04_MATLAB_Conventional: run_conventional_batch.m, sanity_check_vs_truth.m.

# 10. What was achieved

•  conventional_predictions.csv holds 2481 rows: every one of the 827 records for each of the three methods; ND, DT and dual answers are kept.

•  Counts of ND, DT, D1/D2 and PD/T1 (0 since D13) per method and data role are saved (conventional_counts.csv).

•  A plausibility check against the IEC TC 10 benchmark shows the three methods behave sensibly (it is not a result).

•  The file was read back in Python and its size, record order and columns were confirmed.

# 11. Record of this step

| Item | Record |
| --- | --- |
| Step | 16 - Run the three methods on every record |
| Environment | MATLAB, run from Claude Code through the MATLAB MCP connection |
| Completed | 11 October 2026 |
| Status | Done |
| Main inputs | dga_master.csv (827 records, data version 1.0); 02_Standards tables |
| Main outputs | 11_Results/conventional: conventional_predictions.csv, conventional_counts.csv, impact_of_rules.csv, gate_by_class.csv, sanity_agreement_benchmark.csv, README.md |
| Checks | 2481 rows; 827 unique records in master order; result consistent with gate in every row; Python read-back OK |
| Decisions | none new |

# 12. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DF2 | Made in Step 9 from DS1-DS5 (Steps 5-9 programs). Use: All clean records with role, class, flags and original values. | File: 03_Data/processed/dga_master.csv; SHA-256 AE9E6C0C84CF7180... |
| DF5 | Made in Step 12 from ST1-ST4 and P1-P4. Use: Limits used by the conventional methods (Steps 14-17). | File: 02_Standards/*.csv |
| DF6 | Made in Step 13 from all frozen files. Use: SHA-256 of every frozen file; checked by verify_data_version() before every later step. | File: 03_Data/data_version_1.0.sha256; SHA-256 260EBE0C8921E52C... |
| DF9 | Made in Step 16 by run_conventional_batch.m on data version 1.0. Use: Input of the agreement analysis (Step 18 onwards) and of the boundary-distance test (RQ2). | File: 11_Results/conventional/conventional_predictions.csv; SHA-256 30DDD34EEF12AEF6... |
| DF10 | Made in Step 16 by run_conventional_batch.m. Use: Table of unresolved and dual results. | File: 11_Results/conventional/conventional_counts.csv; SHA-256 0467416EBE509875... |
| DF11 | Made in Step 14 by impact_of_rules.m (impact_of_rules.csv and gate_by_class.csv). Use: Evidence for decision D12; gate_by_class.csv SHA-256 E249F9B6899420A56958DCDF934F926492B11DFB24553AF628391F37A3D9F51D. | File: 11_Results/conventional/impact_of_rules.csv; SHA-256 11A215384496E2D3... |
| DF12 | Made in Step 16 by sanity_check_vs_truth.m. Plausibility check only, not a result. Use: Shows the implementations behave plausibly before the formal evaluation. | File: 11_Results/conventional/sanity_agreement_benchmark.csv; SHA-256 A276AA8AC133007D... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |
| SW2 | MATLAB R2025b, version 25.2.0.2998904, The MathWorks, Inc., Natick, MA, USA. Use: Runs the conventional-method functions, unit tests, batch run and Duval figures (Steps 14-17). | https://www.mathworks.com/products/matlab.html |

# 13. How this helps the next steps

Next step: Step 17 [MATLAB] - draw Duval Triangle 1 for each data role, coloured by true class (Figure 4.4).

•  Step 17 draws the Duval Triangles.

•  Step 18 re-implements the methods in Python and checks that MATLAB and Python agree on 100 % of the 2481 rows.

•  Steps 19 to 24 and the statistics stage compare machine learning with these predictions; the boundary_distance column is the input of the boundary-distance regression (RQ2).

# 14. Open items and limitations

•  These counts are descriptive. Nothing here says which method is better; the evaluation measures and tests fixed in the Analysis Plan are applied in later steps.

•  Under the upper gate, 242 of 827 records are called Normal, including 160 true faults; the gate result therefore limits what any conventional method can achieve on low-gas faults. Sensitivity with the lower gate is in the same file (91 records).

•  IEC ND is high (319 raw, 200 after the gate) because T1 now needs CH4/H2 > 1 (D13) and many records have CH4/H2 of 1 or less or undefined; Rogers returns ND for many records because every Rogers case needs all three ratios.

•  The plausibility check uses a simple scoring (dual answers counted correct, DT and ND wrong, raw answers); the formal scoring may differ.

# 15. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| CH4 | methane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| D2 | discharges of high energy | Arcing with power follow-through: extensive carbonisation, metal fusion, sometimes tripping of the equipment. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| T2 | thermal fault 300 to 700 °C | Overheating in which the paper has carbonised. |
| T3 | thermal fault above 700 °C | Very hot fault: carbonised oil, metal colouring (800 °C) or metal fusion (above 1 000 °C). |
| T12 | T1 or T2 (merged class) | Used in this project when a source does not say whether the thermal fault was below or above 300 °C. |
| DT | mixture of thermal and electrical faults | A zone of the Duval Triangle 1 for cases that look partly thermal and partly electrical. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| Ratio method | diagnosis from gas ratios | Divides one gas by another (for example C2H2/C2H4) and compares the result with fixed limits to name the fault. |
| Duval Triangle 1 | graphical DGA method by M. Duval | The shares of CH4, C2H4 and C2H2 are plotted as one point in a triangle divided into fault zones. |
| Rogers ratios | older gas-ratio method by R.R. Rogers | A ratio table that names faults from three gas ratios; kept in IEEE C57.104. |
| Normality gate | rule that lets conventional methods answer 'Normal' | If all gases are below their typical values, the conventional methods give Normal instead of a fault (decision D3). |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Internal test set | Dissanayake unseen test file | 70 records (61 independent of the benchmark) kept away from training. |
| External test set | Li (2019) dataset | 201 records from a different source (86 independent of the benchmark), used to test the models on new data. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| D1-D14 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |
| ND (no diagnosis) | No diagnosis | The answer of a method when no rule applies or a ratio it needs cannot be calculated. It is a result and is never deleted. |
| Dual answer (D1/D2) | Two classes returned together | Sometimes the IEC table fits two fault types at once. The method then answers with both (D1/D2); it counts as correct if the true class is either one. |
| Boundary distance | Distance to the nearest decision boundary | How far a sample is from the line where the diagnosis would change. A small distance means a small measurement error could change the diagnosis. |
| Decade (log10 unit) | A factor of 10 | A distance of 1 decade on the ratio scale means the ratio is 10 times larger or smaller, e.g. from 0.1 to 1. |
| Rogers case | Rogers diagnosis code 0 to 5 | The Rogers table gives each combination of ratios a case number: 0 normal, 1 partial discharge, 2 arcing, 3 and 4 thermal below 700 degrees, 5 thermal above 700 degrees. |
| Raw and final result | Result before and after the normality gate | raw_result is what the method itself says; result is what is left after samples with low gas levels have been called Normal by the gate. |
| Unit test (matlab.unittest) | Automatic test of one small piece of code | A test that feeds a function a known input and checks the answer, so that any later change that breaks the function is noticed at once. |