Step 18 Report

Cross-check MATLAB against Python

Environment: Claude Code (this chat)   |   Completed: 11 October 2026   |   Report version 1 (11 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The three conventional methods were programmed a second time, independently, in Python and run on the same 827 records. The two programs agree on all 2481 of 2481 record-method rows: every diagnosis, every normality-gate flag, every ratio, every Duval percentage and every boundary distance. The largest numerical difference is 3.4E-13, far below the allowed 1e-9. The conventional-method results can therefore be trusted as the baseline for the machine-learning comparison.

# 1. Purpose of this step

The conventional methods (IEC 60599 ratios, Rogers ratios and Duval Triangle 1) are the yardstick against which the machine-learning models will be judged. Before they are used, this step checks that they were coded correctly, by building a second, independent version in another language and comparing the two record by record.

# 2. Method used

## Approach

Independent re-implementation (also called N-version or differential testing): the three conventional methods were programmed a second time, in Python, directly from the specification - the frozen 02_Standards tables and decisions D11, D12 and D13 - and not by translating the MATLAB code. Both programs were then run on the same 827 records and every output was compared, record by record and method by method.

For the Duval boundary distance a deliberately different geometric method was used. MATLAB cuts the zone edges into pieces and keeps the pieces with different zones on each side; Python builds every zone rule as a polygon by half-plane clipping (Sutherland and Hodgman) and measures the distance from the sample point to the nearest polygon of a different zone. Both definitions give the same distance in theory, so agreement checks the geometry two ways.

## Why this method

•  A second, independent program is the strongest practical test that the conventional methods are coded correctly: a coding error would have to be made in exactly the same way in two languages to go unnoticed.

•  The conventional methods are the baseline against which the machine-learning models will be judged; an error in the baseline would bias every comparison in the thesis.

•  The roadmap (Step 18) requires identical diagnoses on 100 % of records and numbers equal within 1e-9.

## Settings and rules

| Setting | Value |
| --- | --- |
| Records and methods | 827 records x 3 methods (IEC 60599, Rogers, Duval Triangle 1) = 2 481 rows |
| Compared outputs | gate_upper, gate_lower, raw_result, result (exact text); ratios R1, R2, R5; Duval percentages; boundary distance |
| Number tolerance | ¦a - b¦ <= 1e-9 x max(1, ¦a¦, ¦b¦); NaN must meet NaN and Inf must meet Inf of the same sign |
| Rules | decisions D11 (gate, ranges, dual answers, Rogers mapping), D12 (ND only for used ratios; Duval distance to decision edges), D13 (IEC T1 needs CH4/H2 > 1) |
| Data | data version 1.0, verified by its SHA-256 manifest before the run |

## Equations

a-b≤10-9⋅max1,a,b#1

where:

a, b  –  the same number computed by Python and by MATLAB (ratio, percentage or boundary distance)

Two values that are both NaN (undefined) or both infinite with the same sign also count as equal.

dD=minr∈ZPcdistP,Πr#2

where:

dD  –  Duval boundary distance of sample P [percentage points, triangle of side 100]

ZPc  –  the rules of Duval Triangle 1 whose zone differs from the zone of P

Πr  –  the polygon of rule r, built by clipping the triangle with the rule's limits

distP,Πr  –  Euclidean distance from P to the polygon (0 if P lies inside or on its edge)

## Tools and programs

•  06_Python_ML/src/conventional/conventional_methods.py (independent implementation) and step18_crosscheck.py (comparison)

•  Python 3.12.10 with numpy 2.5.3 and pandas 3.0.6; 06_Python_ML/tests/test_conventional_python.py (pytest 9.1.1, 45 tests)

## Method references

[M8] I. E. Sutherland and G. W. Hodgman, "Reentrant polygon clipping," Communications of the ACM, vol. 17, no. 1, pp. 32-42, Jan. 1974. https://cacmb4.acm.org/magazines/1974/1/11767-reentrant-polygon-clipping

[M9] IEEE Standard for Floating-Point Arithmetic, IEEE Std 754-2019, 2019. doi: 10.1109/IEEESTD.2019.8766229

# 3. What was done, step by step

1.  Read the specification only: the frozen standards tables in 02_Standards and the decisions D11, D12 and D13 that fix how the tables are applied (normality gate, inclusive ranges, dual answers, when a result is 'no diagnosis', the Rogers class mapping and the boundary distances).

2.  Wrote 06_Python_ML/src/conventional/conventional_methods.py from that specification. The MATLAB code was read only to see which output columns it writes, not copied.

3.  For the Duval boundary distance, used a different geometric method from MATLAB: each zone rule is built as a polygon by clipping the triangle with the rule's limits, and the distance is measured from the sample point to the nearest polygon of another zone.

4.  Checked that data version 1.0 is unchanged (SHA-256 manifest), then ran the Python program on all records and wrote 11_Results/conventional/conventional_predictions_python.csv.

5.  Compared every row with MATLAB's conventional_predictions.csv: the four text outputs must be identical, and the seven numbers equal within 1e-9 (NaN and Inf in the same places). The result is 08_Statistical_Analysis/cross_language_check.csv.

6.  Added automated tests: the 40 published worked examples, edge cases of decisions D11-D13, and a test that the two programs agree on every record.

# 4. What we found

## Agreement between MATLAB and Python

| Method | Raw diagnosis identical | Final result identical | Upper gate identical | Lower gate identical | All numbers within 1e-9 |
| --- | --- | --- | --- | --- | --- |
| IEC60599 | 827 / 827 | 827 / 827 | 827 / 827 | 827 / 827 | 827 / 827 |
| Rogers | 827 / 827 | 827 / 827 | 827 / 827 | 827 / 827 | 827 / 827 |
| Duval | 827 / 827 | 827 / 827 | 827 / 827 | 827 / 827 | 827 / 827 |

In total 2481 of 2481 rows agree in every compared value; the largest numerical difference between the two programs is 3.4E-13 (rounding of the last digits of a double-precision number).

## The same counts from both programs

| Method | No diagnosis (ND) Python / MATLAB | DT zone Python / MATLAB | Dual answers Python / MATLAB | Gated Normal Python / MATLAB |
| --- | --- | --- | --- | --- |
| IEC60599 | 319 / 319 | 0 / 0 | 90 / 90 | 242 / 242 |
| Rogers | 424 / 424 | 0 / 0 | 0 / 0 | 242 / 242 |
| Duval | 2 / 2 | 27 / 27 | 0 / 0 | 242 / 242 |

These are counts before the normality gate (raw results) on all records; they are descriptions of how often each method answers, not yet measures of accuracy, which come in Steps 28 to 32.

# 5. Checks

| Check | Result |
| --- | --- |
| Data version 1.0 unchanged before the run (SHA-256 manifest) | PASS |
| Every record and method present in both programs | 2481 rows - PASS |
| Identical diagnoses and gate flags (roadmap target 100 %) | 2481 of 2481 - PASS |
| Ratios, percentages and distances within 1e-9 | largest difference 3.4E-13 - PASS |
| Published worked examples reproduced by Python (39 Duval, 1 Rogers) | 40 of 40 - PASS |
| Automated test suite (pytest) | 56 of 56 PASS (45 new) |

# 6. Problems and fixes

•  While the Python geometry was being written, it was noticed that converting the triangle coordinates to the drawing plane reverses the direction in which polygon corners are listed. The 'is the point inside this polygon' test was made independent of that direction before the comparison was run. No other problem occurred, and the comparison passed on its first run.

# 7. Decisions

•  No new decision. The Python program implements the decisions already approved for the conventional methods: D11, D12 (rules 1 and 3) and D13.

# 8. Files produced

•  08_Statistical_Analysis/cross_language_check.csv (one row per record and method, Python and MATLAB values side by side)

•  11_Results/conventional/conventional_predictions_python.csv; 03_Data/interim/step18_report.md

•  06_Python_ML/src/conventional/conventional_methods.py and step18_crosscheck.py; 06_Python_ML/tests/test_conventional_python.py

# 9. What was achieved

•  An independent Python implementation of IEC 60599, Rogers and Duval Triangle 1 now exists, written from the standards tables and decisions, not from the MATLAB code.

•  MATLAB and Python agree on all 2 481 record-method rows: every diagnosis, both normality-gate flags, every ratio, every Duval percentage and every boundary distance (largest difference 3.4e-13).

•  The Duval boundary distance was confirmed by two different geometric methods.

•  45 new automated tests (published worked examples, decision edge cases, MATLAB-Python agreement); the whole suite passes 56 of 56.

# 10. Record of this step

| Item | Record |
| --- | --- |
| Step | 18 - Cross-check MATLAB against Python |
| Environment | Claude Code (this chat) |
| Completed | 11 October 2026 |
| Status | Done |
| Main inputs | 11_Results/conventional/conventional_predictions.csv (MATLAB); 02_Standards tables; dga_master.csv (data version 1.0) |
| Main outputs | 08_Statistical_Analysis/cross_language_check.csv; 11_Results/conventional/conventional_predictions_python.csv; conventional_methods.py; step18_report.md |
| Checks | 2 481 of 2 481 rows identical within 1e-9 - PASS; pytest 56 of 56 PASS |
| Decisions | None new (implements D11, D12, D13) |

# 11. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DF2 | Made in Step 9 from DS1-DS5 (Steps 5-9 programs). Use: All clean records with role, class, flags and original values. | File: 03_Data/processed/dga_master.csv; SHA-256 AE9E6C0C84CF7180... |
| DF5 | Made in Step 12 from ST1-ST4 and P1-P4. Use: Limits used by the conventional methods (Steps 14-17). | File: 02_Standards/*.csv |
| DF6 | Made in Step 13 from all frozen files. Use: SHA-256 of every frozen file; checked by verify_data_version() before every later step. | File: 03_Data/data_version_1.0.sha256; SHA-256 260EBE0C8921E52C... |
| DF9 | Made in Step 16 by run_conventional_batch.m on data version 1.0. Use: Input of the agreement analysis (Step 18 onwards) and of the boundary-distance test (RQ2). | File: 11_Results/conventional/conventional_predictions.csv; SHA-256 30DDD34EEF12AEF6... |
| DF15 | Made in Step 18 from DF9 and the Python re-implementation. Use: Record-by-record comparison of the two implementations (diagnoses, ratios, percentages, distances). | File: 08_Statistical_Analysis/cross_language_check.csv; SHA-256 98BD1C1F24034B3E... |
| DF16 | Made in Step 18 from data version 1.0 and the 02_Standards tables. Use: Independent Python version of DF9 (same columns). | File: 11_Results/conventional/conventional_predictions_python.csv; SHA-256 E13BB8D97CFB1FAF... |
| DF17 | Written in Step 18 from the 02_Standards tables and decisions D11-D13 (not translated from MATLAB). Use: Independent implementation of IEC 60599, Rogers and Duval Triangle 1; reused in Step 19 onwards. | File: 06_Python_ML/src/conventional/conventional_methods.py; SHA-256 3FF606094A010706... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |
| SW2 | MATLAB R2025b, version 25.2.0.2998904, The MathWorks, Inc., Natick, MA, USA. Use: Runs the conventional-method functions, unit tests, batch run and Duval figures (Steps 14-17). | https://www.mathworks.com/products/matlab.html |

# 12. How this helps the next steps

Next step: Step 19: build the machine-learning preprocessing and feature pipelines (scikit-learn) for the four feature sets of the Analysis Plan, with scaling, class weighting and any oversampling fitted inside the training folds only.

•  The conventional-method results can now be trusted as the baseline for Steps 28-32 (McNemar and Cochran tests, Cohen's kappa, and the boundary-distance logistic regression all use these predictions and distances).

•  The Python implementation will be reused by the diagnosis service (Step 38), so the service gives exactly the same conventional answers as MATLAB.

•  Step 19 builds the machine-learning preprocessing and feature pipelines on the same frozen data.

# 13. Open items and limitations

•  Agreement proves that both programs apply the same rules; it does not prove that the rules are the right reading of the standards. The standards values still marked TO VERIFY (Duval Triangle 1 from secondary sources, Rogers from a copy not licensed to the researcher, IEC against the 2022 text) remain open.

•  The approved normality gate (D11) calls 242 of the 827 records Normal, and 160 of them are true faults (from gate_by_class.csv of Step 16). This will lower the conventional methods' scores and must be discussed in the thesis; the lower-end gate is the planned sensitivity analysis.

# 14. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| CH4 | methane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| DT | mixture of thermal and electrical faults | A zone of the Duval Triangle 1 for cases that look partly thermal and partly electrical. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| Duval Triangle 1 | graphical DGA method by M. Duval | The shares of CH4, C2H4 and C2H2 are plotted as one point in a triangle divided into fault zones. |
| Rogers ratios | older gas-ratio method by R.R. Rogers | A ratio table that names faults from three gas ratios; kept in IEEE C57.104. |
| Normality gate | rule that lets conventional methods answer 'Normal' | If all gases are below their typical values, the conventional methods give Normal instead of a fault (decision D3). |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Logistic regression | multinomial logistic regression | A simple, explainable model that turns weighted gas values into class probabilities. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Fold | one part of the cross-validation split | Here the training data are cut into 5 folds (parts). |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| pytest | Python testing tool | Runs the automated checks that prove the data rules hold. |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| D1-D14 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |
| Primary and secondary source | the original document and a document that quotes it | Values from a secondary source are marked TO VERIFY until checked against the primary source. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| R1, R2, R5 | Rogers gas ratios | R1 = CH4/H2, R2 = C2H2/C2H4, R5 = C2H4/C2H6; the three ratios the Rogers method compares with its table. |
| ND (no diagnosis) | No diagnosis | The answer of a method when no rule applies or a ratio it needs cannot be calculated. It is a result and is never deleted. |
| Dual answer (D1/D2) | Two classes returned together | Sometimes the IEC table fits two fault types at once. The method then answers with both (D1/D2); it counts as correct if the true class is either one. |
| Boundary distance | Distance to the nearest decision boundary | How far a sample is from the line where the diagnosis would change. A small distance means a small measurement error could change the diagnosis. |
| Raw and final result | Result before and after the normality gate | raw_result is what the method itself says; result is what is left after samples with low gas levels have been called Normal by the gate. |
| Polygon clipping (Sutherland-Hodgman) | Cutting a shape with straight lines | A standard way to find the area of the triangle that satisfies one limit after another; used to draw the Duval zones from their limits. |
| Unit test (matlab.unittest) | Automatic test of one small piece of code | A test that feeds a function a known input and checks the answer, so that any later change that breaks the function is noticed at once. |