Step 20 Report

Train and tune the classifiers (nested cross-validation)

Environment: Claude Code (this chat)   |   Completed: 11 October 2026   |   Report version 1 (11 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: All six models were trained and tuned on all four feature sets with nested cross-validation: 1200 outer-fold tasks, each with its own inner search for the best settings, using only the 439 development records. The highest mean macro-F1 over the 50 outer folds was 0.850 (SD 0.038), for Random Forest on feature set F4; the majority baseline reached 0.046. These are development-set estimates; no model has been chosen yet (Step 21) and no test set has been opened (Step 22). Re-running saved tasks reproduced the results exactly.

# 1. Purpose of this step

This step measures how well each approved model, with each feature set, can recognise the seven classes (Normal, PD, D1, D2, T1, T2, T3), with its settings tuned fairly and its performance measured on records it never saw during training or tuning. The results feed the written model-selection rule in Step 21.

# 2. Method used

## Approach

Nested cross-validation. The outer loop uses the 50 fixed train/test splits of Step 10 (5 folds x 10 repeats). Inside each outer training part, an inner 5-fold cross-validation tries every setting in the model's search grid and keeps the one with the highest macro-F1. That setting is refitted on the whole outer training part and then predicts the outer held-out fold, which played no part in training or tuning.

This was done for all 6 models on all 4 feature sets: 6 x 4 x 50 = 1 200 outer-fold tasks, each with its own inner search. For every held-out record the predicted class and the probability of every class were saved, together with the chosen setting and all performance measures of Analysis Plan Section 6.

## Why this method

•  If the same data are used both to choose settings and to measure performance, the measured performance is too optimistic; nested cross-validation keeps tuning and measurement apart (Varma and Simon, 2006) and is the approved design (plan item 10).

•  Fifty outer folds give 50 paired estimates for every model, which the statistical comparisons of Step 30 (Friedman, Nemenyi, corrected resampled t-test) require.

•  Saving every prediction and probability means that any later measure or figure can be recomputed without training again.

## Settings and rules

| Setting | Value |
| --- | --- |
| Outer loop | 50 fixed folds from folds.csv (stratified, near-duplicate groups kept together) |
| Inner loop | StratifiedGroupKFold(5), near-duplicate groups kept together (D17); seed 20261010 + 1000 x repeat + fold |
| Tuning score | macro-F1 (approved primary measure) |
| Search grids | Analysis Plan 5.2: SVM 20, Random Forest 9, XGBoost 18, MLP 9, logistic regression 3 combinations; baseline none |
| Records | 439 development records only - the test sets were not opened |
| Execution | 6 parallel processes, single-threaded models (results independent of the number of workers); run time 2 h 42 min |
| Software | Python 3.12.10, scikit-learn 1.9.1, xgboost 3.4.1 |

## Equations

Macro-F1=1Kc=1KF1c#1

where:

Macro-F1  –  unweighted mean of the per-class F1-scores (Analysis Plan Eq. 17); K = 7 classes

F1c  –  harmonic mean of precision and recall of class c on the held-out fold

m=150i=150mi  s=149i=150mi-m2#2

where:

mi  –  a measure (e.g. macro-F1) on outer fold i

m, s  –  mean and standard deviation over the 50 outer folds, as reported in Table 4.4

## Tools and programs

•  06_Python_ML/src/ml/step20_nested_cv.py (runs the tasks; resumable), step20_summarize.py (Table 4.4, completeness, reproducibility)

•  scikit-learn GridSearchCV and StratifiedGroupKFold; joblib for parallel processes

## Method references

[M13] S. Varma and R. Simon, "Bias in error estimation when using cross-validation for model selection," BMC Bioinformatics, vol. 7, art. 91, 2006. doi: 10.1186/1471-2105-7-91

[M3] F. Pedregosa et al., "Scikit-learn: Machine Learning in Python," Journal of Machine Learning Research, vol. 12, pp. 2825-2830, 2011. https://jmlr.org/papers/v12/pedregosa11a.html

[M10] T. Chen and C. Guestrin, "XGBoost: A Scalable Tree Boosting System," in Proc. 22nd ACM SIGKDD Int. Conf. Knowledge Discovery and Data Mining (KDD '16), pp. 785-794, 2016. doi: 10.1145/2939672.2939785

# 3. What was done, step by step

1.  Recorded the remaining design details as decision D17 (inner folds keep near-duplicate groups together, deterministic seeds, what is saved, test sets closed).

2.  Wrote the experiment program (step20_nested_cv.py). Each of the 1 200 tasks saves its result file only when it has finished, so an interrupted run can resume without redoing work.

3.  Tested the program on a few tasks and timed one task of every model (about 3 minutes per fold and feature set in total, mostly XGBoost and Random Forest), then ran the full experiment in the background with parallel processes.

4.  Collected all task results into fold_metrics.csv and predictions.csv, checked completeness, computed Table 4.4, and re-ran saved tasks from their configuration to prove reproducibility (step20_summarize.py).

# 4. What we found

## Table 4.4 - cross-validation results (mean and SD over 50 outer folds)

| Set | Model | Macro-F1 mean (SD) | Balanced accuracy mean (SD) | Kappa | MCC | Average rank |
| --- | --- | --- | --- | --- | --- | --- |
| F1 | Majority baseline | 0.046 (0.000) | 0.143 (0.000) | 0.000 | 0.000 | 22.50 |
| F1 | Logistic regression | 0.808 (0.036) | 0.820 (0.036) | 0.788 | 0.791 | 10.30 |
| F1 | SVM (RBF) | 0.804 (0.035) | 0.817 (0.035) | 0.783 | 0.785 | 10.76 |
| F1 | Random Forest | 0.773 (0.049) | 0.778 (0.050) | 0.757 | 0.760 | 14.87 |
| F1 | XGBoost | 0.771 (0.049) | 0.776 (0.049) | 0.755 | 0.758 | 14.80 |
| F1 | Neural network (MLP) | 0.793 (0.044) | 0.798 (0.043) | 0.778 | 0.780 | 11.88 |
| F2 | Majority baseline | 0.046 (0.000) | 0.143 (0.000) | 0.000 | 0.000 | 22.50 |
| F2 | Logistic regression | 0.742 (0.045) | 0.760 (0.047) | 0.708 | 0.711 | 18.06 |
| F2 | SVM (RBF) | 0.794 (0.038) | 0.810 (0.038) | 0.767 | 0.770 | 12.48 |
| F2 | Random Forest | 0.805 (0.041) | 0.811 (0.041) | 0.784 | 0.786 | 10.62 |
| F2 | XGBoost | 0.788 (0.041) | 0.790 (0.042) | 0.767 | 0.770 | 13.30 |
| F2 | Neural network (MLP) | 0.765 (0.032) | 0.769 (0.034) | 0.739 | 0.741 | 15.74 |
| F3 | Majority baseline | 0.046 (0.000) | 0.143 (0.000) | 0.000 | 0.000 | 22.50 |
| F3 | Logistic regression | 0.821 (0.038) | 0.833 (0.039) | 0.801 | 0.803 | 7.76 |
| F3 | SVM (RBF) | 0.810 (0.041) | 0.823 (0.042) | 0.790 | 0.793 | 9.62 |
| F3 | Random Forest | 0.824 (0.036) | 0.832 (0.035) | 0.807 | 0.809 | 7.00 |
| F3 | XGBoost | 0.833 (0.041) | 0.836 (0.041) | 0.818 | 0.820 | 6.04 |
| F3 | Neural network (MLP) | 0.795 (0.044) | 0.797 (0.043) | 0.777 | 0.779 | 12.14 |
| F4 | Majority baseline | 0.046 (0.000) | 0.143 (0.000) | 0.000 | 0.000 | 22.50 |
| F4 | Logistic regression | 0.820 (0.039) | 0.832 (0.040) | 0.800 | 0.802 | 8.14 |
| F4 | SVM (RBF) | 0.819 (0.038) | 0.831 (0.037) | 0.801 | 0.804 | 8.05 |
| F4 | Random Forest | 0.850 (0.038) | 0.857 (0.039) | 0.838 | 0.840 | 3.30 |
| F4 | XGBoost | 0.842 (0.039) | 0.845 (0.037) | 0.832 | 0.834 | 4.58 |
| F4 | Neural network (MLP) | 0.805 (0.040) | 0.808 (0.040) | 0.792 | 0.794 | 10.56 |

Average rank: within each of the 50 outer folds the 24 model-feature combinations are ranked by macro-F1 (1 = best) and the ranks are averaged. It is descriptive only; whether the differences are statistically significant is tested in Step 30 (Friedman and Nemenyi tests), and the final choice follows the written rule in Step 21.

•  Feature set F1: highest mean macro-F1 0.808 (Logistic regression), lowest 0.771 (XGBoost).

•  Feature set F2: highest mean macro-F1 0.805 (Random Forest), lowest 0.742 (Logistic regression).

•  Feature set F3: highest mean macro-F1 0.833 (XGBoost), lowest 0.795 (Neural network (MLP)).

•  Feature set F4: highest mean macro-F1 0.850 (Random Forest), lowest 0.805 (Neural network (MLP)).

Every classifier was far above the majority baseline. The fold-to-fold standard deviations (about 0.03 to 0.05) are of the same size as many of the gaps between pipelines, so the order in Table 4.4 must not be read as a ranking of significance; Step 21 applies the written test to the best and the next pipeline.

## F1-score per fault class (mean over 50 folds), best feature set of each model

| Model (feature set) | Normal | PD | D1 | D2 | T1 | T2 | T3 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Majority baseline (any set) | 0.000 | 0.000 | 0.000 | 0.324 | 0.000 | 0.000 | 0.000 |
| Logistic regression (F3) | 0.879 | 0.818 | 0.694 | 0.810 | 0.853 | 0.768 | 0.926 |
| SVM (RBF) (F4) | 0.894 | 0.768 | 0.736 | 0.817 | 0.861 | 0.739 | 0.917 |
| Random Forest (F4) | 0.905 | 0.828 | 0.775 | 0.864 | 0.876 | 0.762 | 0.941 |
| XGBoost (F4) | 0.911 | 0.791 | 0.766 | 0.863 | 0.876 | 0.761 | 0.930 |
| Neural network (MLP) (F4) | 0.890 | 0.711 | 0.697 | 0.816 | 0.864 | 0.746 | 0.912 |

The two classes with the lowest F1 were, for each model: Logistic regression: D1 and T2; SVM (RBF): D1 and T2; Random Forest: T2 and D1; XGBoost: T2 and D1; Neural network (MLP): D1 and PD. D1 (low-energy discharge) borders D2 (high-energy discharge), and T2 lies between T1 and T3; the zones of the conventional methods (IEC ratios, Duval Triangle) also meet at these classes, so overlapping gas patterns are a plausible reason. Label quality may also contribute (the labelling method of the development data is not documented). This is an interpretation for the thesis discussion, to be checked with the confusion matrices in Chapter 4.

# 5. Checks

| Check | Result |
| --- | --- |
| Data version 1.0 unchanged (SHA-256 manifest) | PASS |
| Only development records read (the three test sets stay closed) | PASS - no test record read |
| Completeness (6 models x 4 feature sets x 50 folds) | PASS (1200 of 1200 tasks) |
| Every development record predicted once per repeat, model and feature set | PASS (105360 prediction rows) |
| Tasks with any warning | 5 |
| Reproducibility: saved tasks re-run from their configuration | PASS (4 tasks re-run; identical predictions, settings and probabilities) |

# 6. Problems and fixes

•  Run time: before the run, the expected time (about 11 processor-hours) was measured on single tasks, and the program was made resumable so that an interruption (for example the computer going to sleep) would not lose work. The run finished without interruption or error.

•  Warnings: 5 of the 1 200 tasks each reported one convergence warning, all from the neural network (MLP) on feature set F2 (gas percentages). Each MLP task fits the network 46 times (9 settings x 5 inner folds, plus the final refit), so about 9 200 network fits gave 5 warnings; the saved results do not show whether a warning came from an inner tuning fit or from the final refit. These tasks were kept as they are (removing them would bias the comparison). A likely contributor is that the five percentages of F2 always add up to 100 %, so one input is fully determined by the others; this is not proven. MLP on F2 is not among the leading pipelines (Table 4.4), so the warnings do not affect the model choice in Step 21.

# 7. Decisions

•  D17 (procedural, within the approved plan): inner folds keep near-duplicate groups together; deterministic inner seeds; every prediction and probability saved; test sets closed; parallel single-threaded tasks with checkpoints.

# 8. Files produced

•  07_Experiments/2026-10-11_nestedcv_v1/: config.yaml, run_info.json, tasks/ (1 200 result files and 1 200 prediction files), fold_metrics.csv, predictions.csv, reproducibility_check.csv

•  11_Results/tables/T4_4_cv_results.csv (Table 4.4); 03_Data/interim/step20_report.md

•  06_Python_ML/src/ml/step20_nested_cv.py and step20_summarize.py

# 9. What was achieved

•  All 1200 outer-fold tasks finished; every development record was predicted once per repeat for every model and feature set.

•  Table 4.4 gives, for all 24 model-feature combinations, the mean and standard deviation over 50 folds of macro-F1 and the secondary measures.

•  Every fold's chosen setting, measures, predictions and class probabilities are saved, so later statistics need no retraining.

•  Re-running saved tasks from their configuration reproduced exactly the same predictions, settings and scores.

# 10. Record of this step

| Item | Record |
| --- | --- |
| Step | 20 - Train and tune the classifiers (nested cross-validation) |
| Environment | Claude Code (this chat) |
| Completed | 11 October 2026 |
| Status | Done |
| Main inputs | dga_master.csv and folds.csv (data version 1.0); configs/ml_config.yaml; the 24 pipelines of Step 19 |
| Main outputs | 07_Experiments/2026-10-11_nestedcv_v1 (tasks, fold_metrics.csv, predictions.csv, run_info.json); 11_Results/tables/T4_4_cv_results.csv |
| Checks | completeness PASS (1200 of 1200 tasks); reproducibility PASS (4 tasks re-run; identical predictions, settings and probabilities); test sets opened: no |
| Decisions | D17 (inner-loop and run details; procedural) |

# 11. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DF2 | Made in Step 9 from DS1-DS5 (Steps 5-9 programs). Use: All clean records with role, class, flags and original values. | File: 03_Data/processed/dga_master.csv; SHA-256 AE9E6C0C84CF7180... |
| DF3 | Made in Step 10 from DF2. Use: Fold number of every training record in each of 10 repeats. | File: 03_Data/processed/folds.csv; SHA-256 0CE7D9AF3C7CE9F6... |
| DF6 | Made in Step 13 from all frozen files. Use: SHA-256 of every frozen file; checked by verify_data_version() before every later step. | File: 03_Data/data_version_1.0.sha256; SHA-256 260EBE0C8921E52C... |
| DF18 | Written in Step 19 from the Analysis Plan (Sections 5.1-5.4) and decisions D6, D15, D16. Use: Feature sets, preprocessing, models and search grids used in Steps 19-24. | File: 06_Python_ML/configs/ml_config.yaml; SHA-256 C78C864AEC6751F8... |
| DF20 | Written in Step 19. Use: Feature builder (F1-F4), imputation, scaling, class weights and the six classifiers. | File: 06_Python_ML/src/ml/pipelines.py; SHA-256 8A7131A059C7BDED... |
| DF21 | Produced in Step 20 by step20_nested_cv.py (run 2026-10-11_nestedcv_v1, 21:01-23:44, 6 workers). Use: Chosen setting, inner score and all Section 6 measures of every outer-fold task (6 models x 4 feature sets x 50 folds). | File: 07_Experiments/2026-10-11_nestedcv_v1/fold_metrics.csv; SHA-256 5215981A5636EF1E... |
| DF22 | Produced in Step 20 by step20_summarize.py from DF21. Use: Mean and SD over 50 outer folds of macro-F1 and secondary measures, per-class F1, average rank. | File: 11_Results/tables/T4_4_cv_results.csv; SHA-256 B7D7454BDE778667... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 12. How this helps the next steps

Next step: Step 21: select the final model by the written rule - the highest mean outer-fold macro-F1; if the best and the next model are not significantly different (corrected resampled t-test), the simpler model is chosen - before any test set is opened.

•  Step 21 applies the written selection rule to these results: the highest mean outer-fold macro-F1, and the simpler model if the best two are not significantly different.

•  Steps 30 and 32 draw Figure 4.6 (box plots of the 50 fold values) and Figure 4.7 (critical-difference diagram) and run the Friedman and Nemenyi tests directly from the saved fold results.

•  The saved probabilities support the calibration and uncertainty displays of the dashboard (Step 38 onwards).

# 13. Open items and limitations

•  These are cross-validation estimates on the development data only; how well the chosen model generalises is measured once, on the three test sets, in Step 22.

•  The development labels come from the Dissanayake dataset, whose labelling method is not documented (see the register); the inspection-based IEC TC 10 benchmark in Step 22 is the stronger test.

# 14. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| D2 | discharges of high energy | Arcing with power follow-through: extensive carbonisation, metal fusion, sometimes tripping of the equipment. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| T2 | thermal fault 300 to 700 °C | Overheating in which the paper has carbonised. |
| T3 | thermal fault above 700 °C | Very hot fault: carbonised oil, metal colouring (800 °C) or metal fusion (above 1 000 °C). |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| Duval Triangle 1 | graphical DGA method by M. Duval | The shares of CH4, C2H4 and C2H2 are plotted as one point in a triangle divided into fault zones. |
| SVM | support vector machine | A classifier that separates classes with the widest possible boundary. |
| Random Forest | random forest | Many decision trees, each trained on a random sample; they vote for the answer. |
| XGBoost | extreme gradient boosting | Decision trees built one after another, each correcting the errors of the previous ones. |
| MLP | multilayer perceptron | A small artificial neural network with layers of connected units. |
| Logistic regression | multinomial logistic regression | A simple, explainable model that turns weighted gas values into class probabilities. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Cross-validation | repeated train-and-test on parts of the training data | The data are split into parts; each part is used once for testing while the others train the model. |
| Fold | one part of the cross-validation split | Here the training data are cut into 5 folds (parts). |
| Stratified group k-fold | splitting method | Every part has the same mix of fault classes, and near-identical records stay together in one part. |
| Random seed | starting number for the random shuffle | Recording it means the same split can be made again exactly (seed 20261010). |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| D1-D18 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |
| Primary and secondary source | the original document and a document that quotes it | Values from a secondary source are marked TO VERIFY until checked against the primary source. |
| Pipeline | chain of processing steps and a model | Feature building, imputation, scaling and the classifier joined so that they are always fitted together on the same training rows. |
| Feature set (F1-F4) | the inputs given to a model | F1 log gases, F2 gas percentages, F3 log-ratios and Duval percentages, F4 all of them (Analysis Plan 5.1). |
| Imputation | filling in an undefined value | An undefined Duval percentage is replaced by the median of the training fold (decision D15). |
| Class weight | importance given to each record in training | w_c = N/(K n_c): rare classes get more weight so that every class counts equally (Analysis Plan Eq. 14). |
| Nested cross-validation | cross-validation inside cross-validation | The inner loop chooses the settings, the outer loop measures performance on data the tuning never saw. |
| Hyperparameter grid | list of settings tried for a model | For example C and gamma of the SVM; the best combination is chosen in the inner loop (Analysis Plan 5.2). |
| Macro-F1 | average F1 score over the classes | The primary performance measure; every class counts equally however rare it is. |
| Platt scaling (calibration) | turning SVM scores into probabilities | A sigmoid curve fitted on internal cross-validation scores gives class probabilities (decision D16). |
| SD | standard deviation | How much the 50 fold values spread around their mean; a small SD means the result is stable from fold to fold. |
| Balanced accuracy | mean of the per-class recalls | The share of each class that is found, averaged over the classes, so a rare class counts as much as a common one. |
| Kappa | Cohen's kappa | Agreement between predicted and true classes after removing the agreement expected by chance: 0 = chance, 1 = perfect. |
| MCC | Matthews correlation coefficient | One score from -1 to 1 that uses the whole confusion matrix; 0 means no better than guessing. |
| F1-score (per class) | harmonic mean of precision and recall | High only when the model both finds the records of a class and is rarely wrong when it names that class. |
| Corrected resampled t-test | test for two models compared on the same folds | A t-test whose variance is enlarged because cross-validation folds share training records (Nadeau and Bengio, 2003; Analysis Plan Eq. 28). |
| Friedman and Nemenyi tests | rank-based comparison of several models | Friedman tests whether models' average ranks over the folds differ; Nemenyi then shows which pairs differ (Step 30). |
| Majority baseline | reference model | Always predicts the most common class; any useful model must do clearly better. |
| Average rank | mean position among the compared models | In every fold the models are ranked by macro-F1 (1 = best); the ranks are then averaged over the folds. |
| Convergence warning | training stopped at its step limit | The training algorithm used all allowed iterations before reaching its stopping tolerance; the result may be slightly less than optimal. |
| RBF | radial basis function | The kernel that lets the SVM draw curved boundaries between classes. |