Step 22 Report

Fit the final model and predict the test sets once

Environment: Claude Code (this chat)   |   Completed: 12 October 2026   |   Report version 1 (12 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The chosen model (Random Forest on F4) was fitted on the 439 development records and saved before any test record was used. The three test sets were then predicted once. First-look macro-F1: internal test 0.812 (cross-validation estimate 0.850), IEC TC 10 power transformers 0.731, Li 2019 0.595. Scores fall as the test data move further from the training source - the usual pattern for a model tested on other laboratories' data. Formal confidence intervals and the comparison with the conventional methods follow in Steps 28-30.

# 1. Purpose of this step

This step gives the first honest measure of how the final model performs on records it has never seen in any form: the internal test set from the same source, the inspection-confirmed IEC TC 10 benchmark, and the Li 2019 set from another publication.

# 2. Method used

## Approach

The pipeline chosen in Step 21 (Random Forest on feature set F4) was tuned once more on all 439 development records, with the same settings grid and the same inner procedure as in Step 20, and then fitted on all of them. The fitted pipeline was saved, with its SHA-256 fingerprint, before any test record was touched.

The three test sets - the internal test set, the IEC TC 10 benchmark and the Li 2019 set - were then predicted once, in a single call. A log file records each action with its time and fingerprint, and the program refuses to run a second time.

A first-look score was computed on the evaluation sets approved earlier (decision D19). The formal measures with 95 % confidence intervals and the comparison with the conventional methods follow in Steps 28 to 30.

## Why this method

•  Using every development record for the final fit gives the model the most information; the cross-validation of Step 20 already estimated how well this procedure works (Varma and Simon, 2006).

•  Opening each test set only once, after the model is fixed, means the test results cannot have influenced any choice - the condition for an honest, publishable estimate.

•  Saving the fitted model before the test prediction, with its fingerprint, proves that the model was not changed after the test sets were seen.

## Settings and rules

| Setting | Value |
| --- | --- |
| Pipeline | Random Forest (500 trees, class weights) on F4 (18 features), from Step 21 |
| Final tuning | GridSearchCV over 9 settings; StratifiedGroupKFold(5), near-duplicate groups kept together; seed 20261010; macro-F1. Chosen: max_depth = none, min_samples_leaf = 1 |
| Training records | 439 development records only |
| Test records | 388, predicted once: internal test 70, IEC TC 10 117, Li 2019 201 |
| Primary evaluation sets (D19) | internal test: 61 independent records, 7 classes; IEC TC 10: 58 power transformers, 5 merged classes; Li 2019: 86 independent records, 6 fault classes |
| Scoring rule (IEC TC 10) | T1 or T2 predicted for a T1/T2 record counts as correct; a Normal prediction counts as wrong (Analysis Plan item 6) |
| Software | Python 3.12.10, scikit-learn 1.9.1 |

## Equations

Macro-F1S=1CSc∈CSF1c#1

where:

CS  –  the classes scored on evaluation set S (7, 5 merged, or 6 fault classes)

F1c  –  F1-score of class c on that set; a class counts equally however few records it has

## Tools and programs

•  06_Python_ML/src/ml/step22_final_fit.py (final tuning, saving, one-time prediction, access log; --score-only recomputes the first-look scores from the saved predictions without predicting again)

•  scikit-learn GridSearchCV, StratifiedGroupKFold and metrics; joblib for saving the fitted pipeline

## Method references

[M13] S. Varma and R. Simon, "Bias in error estimation when using cross-validation for model selection," BMC Bioinformatics, vol. 7, art. 91, 2006. doi: 10.1186/1471-2105-7-91

[M3] F. Pedregosa et al., "Scikit-learn: Machine Learning in Python," Journal of Machine Learning Research, vol. 12, pp. 2825-2830, 2011. https://jmlr.org/papers/v12/pedregosa11a.html

# 3. What was done, step by step

1.  Recorded the remaining details as decision D19 (final tuning, saving before testing, run-once rule, evaluation sets) before running anything.

2.  Wrote step22_final_fit.py and checked its scoring part on made-up predictions in a temporary folder (no test record and no model involved).

3.  Ran the step once. The access log shows: final pipeline fitted and saved (2026-10-12T00:11:35), test sets opened and predicted (2026-10-12T00:11:35), predictions written with their fingerprint.

4.  Re-computed the scores from the saved predictions to add the confusion-matrix file (the fingerprint of the predictions did not change), and confirmed that a second full run is refused.

# 4. What we found

## Final setting chosen on all development records

Best setting: max_depth = none, min_samples_leaf = 1; inner-loop macro-F1 0.864; fit time 20.6 s; 0 warnings. This is also the setting chosen most often in the 50 outer folds of Step 20 (Step 21 report).

## First-look scores on the test sets

| Evaluation set | Role | Records | Macro-F1 | Accuracy | Balanced accuracy | Kappa | Called Normal |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Internal test - independent | primary | 61 | 0.812 | 0.820 | 0.816 | 0.790 | 7 |
| Internal test - all | sensitivity | 70 | 0.831 | 0.829 | 0.829 | 0.800 | 7 |
| IEC TC 10 - power transformers | primary | 58 | 0.731 | 0.724 | 0.726 | 0.597 | 1 |
| IEC TC 10 - all | sensitivity | 117 | 0.745 | 0.761 | 0.733 | 0.667 | 1 |
| Li 2019 - independent | primary | 86 | 0.595 | 0.628 | 0.587 | 0.547 | 7 |
| Li 2019 - all (merged classes) | sensitivity | 201 | 0.714 | 0.711 | 0.703 | 0.632 | 8 |

For comparison, the cross-validation estimate on the development data was macro-F1 0.850 (SD 0.038). The model always gives a diagnosis, so its coverage is 100 % and its strict and conditional accuracy are equal. 'Called Normal' counts fault records that the model called Normal; on IEC TC 10 and Li 2019 every such answer is wrong, because these sets contain only faulty units.

## Confusion matrix - Internal test - independent (rows: true class; columns: predicted class)

| True \ predicted | Normal | PD | D1 | D2 | T1 | T2 | T3 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Normal | 7 | 1 | 0 | 0 | 1 | 0 | 1 |
| PD | 0 | 5 | 2 | 0 | 0 | 0 | 0 |
| D1 | 0 | 0 | 6 | 1 | 0 | 0 | 0 |
| D2 | 0 | 0 | 2 | 6 | 0 | 0 | 0 |
| T1 | 0 | 1 | 0 | 0 | 9 | 0 | 0 |
| T2 | 0 | 0 | 0 | 0 | 0 | 9 | 1 |
| T3 | 0 | 0 | 0 | 1 | 0 | 0 | 8 |

## Confusion matrix - IEC TC 10 - power transformers (rows: true class; columns: predicted class)

| True \ predicted | PD | D1 | D2 | T12 | T3 | Normal |
| --- | --- | --- | --- | --- | --- | --- |
| PD | 1 | 0 | 0 | 0 | 0 | 0 |
| D1 | 0 | 7 | 3 | 0 | 0 | 0 |
| D2 | 0 | 3 | 24 | 0 | 0 | 0 |
| T12 | 0 | 0 | 1 | 5 | 1 | 1 |
| T3 | 0 | 0 | 2 | 5 | 5 | 0 |
| Normal | 0 | 0 | 0 | 0 | 0 | 0 |

## Confusion matrix - Li 2019 - independent (rows: true class; columns: predicted class)

| True \ predicted | PD | D1 | D2 | T1 | T2 | T3 | Normal |
| --- | --- | --- | --- | --- | --- | --- | --- |
| PD | 4 | 1 | 0 | 3 | 0 | 0 | 0 |
| D1 | 0 | 17 | 6 | 0 | 0 | 0 | 0 |
| D2 | 0 | 2 | 4 | 0 | 0 | 1 | 0 |
| T1 | 4 | 0 | 0 | 7 | 1 | 2 | 5 |
| T2 | 0 | 0 | 0 | 1 | 4 | 2 | 2 |
| T3 | 0 | 0 | 1 | 0 | 1 | 18 | 0 |
| Normal | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

## What the errors show

•  Internal test (same source as the training data): macro-F1 0.812, 0.038 below the cross-validation estimate - about one fold-to-fold SD (0.038); 11 of 61 records were misclassified, and the only repeated errors were PD called D1 (2), D2 called D1 (2); every other error occurred once.

•  IEC TC 10 power transformers: the discharge classes are recognised well (D2: 24 of 27), but D1 and D2 are confused in both directions (3 each), and only 5 of the 12 T3 records were called T3 - 5 were called T1/T2. In this set PD has a single record, so that one record decides one fifth of the macro-F1.

•  Li 2019: the weakest class is T1 - of 19 T1 records, 7 were recognised, 5 were called Normal and 4 PD. Low-temperature faults often produce only small amounts of gas and can look like a healthy unit or a partial discharge; a different laboratory and label mapping (Li 2019 is a sensitivity set by plan item 3) add to this.

These patterns are informative rather than surprising: the thermal-severity boundary (T2/T3) and the low-energy boundary (Normal/PD/T1) are also where the conventional methods' zones meet. Whether the model is better or worse than the conventional methods on the same records is tested formally in Steps 29-30.

# 5. Checks

| Check | Result |
| --- | --- |
| Data version 1.0 unchanged (SHA-256 manifest) | PASS |
| Fitted pipeline saved with fingerprint before any test prediction | PASS - 1C46D10391429385... |
| Log shows the test sets were opened once, in this step | PASS - 1 opening, 2026-10-12T00:11:35 |
| A second full run is refused | PASS - program stops: predictions already exist |
| Predictions unchanged after re-scoring | PASS - same SHA-256 |
| Every test record predicted exactly once | PASS - 388 rows, 388 records |

# 6. Problems and fixes

•  The first check of the scoring code on made-up data stopped on records without a class label; the real evaluation sets have none, but an explicit check was added so that the real run would stop with a clear message instead. No problem occurred in the real run.

# 7. Decisions

•  D19 (procedural, within the approved plan): final tuning on all development records with the Step 20 inner procedure; model saved before testing; one-time prediction with log and run-once guard; evaluation sets and scoring as approved (plan items 2, 3, 6, 8; decision D9).

# 8. Files produced

•  07_Experiments/2026-10-12_final_fit/: final_pipeline.joblib, final_fit.json, inner_cv_results.csv

•  11_Results/ml/: ml_predictions.csv, ml_first_look.csv, ml_first_look_confusion.csv, test_set_access.log; 03_Data/interim/step22_report.md

•  06_Python_ML/src/ml/step22_final_fit.py

# 9. What was achieved

•  The final model was fitted on the development data only and saved with its fingerprint before any test record was predicted.

•  All 388 test records were predicted once; the access log and the run-once guard document this.

•  First-look macro-F1: internal test 0.812, IEC TC 10 power transformers 0.731, Li 2019 0.595.

# 10. Record of this step

| Item | Record |
| --- | --- |
| Step | 22 - Fit the final model and predict the test sets once |
| Environment | Claude Code (this chat) |
| Completed | 12 October 2026 |
| Status | Done |
| Main inputs | 07_Experiments/model_selection.md; dga_master.csv and folds.csv (data version 1.0) |
| Main outputs | 11_Results/ml/ml_predictions.csv, ml_first_look.csv, ml_first_look_confusion.csv, test_set_access.log; 07_Experiments/2026-10-12_final_fit/ |
| Checks | test sets predicted once (log); second run refused; predictions fingerprint unchanged after re-scoring |
| Decisions | D19 (final fit and evaluation sets; procedural) |

# 11. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DS1 | M. Duval and A. dePablo, "Interpretation of gas-in-oil analysis using new IEC publication 60599 and IEC TC 10 databases," IEEE Electrical Insulation Magazine, vol. 17, no. 2, pp. 31-41, Mar./Apr. 2001. Use: Main benchmark (labels confirmed by inspection): primary analysis = 58 power transformers (codes P, U); sensitivity = all 117. | https://doi.org/10.1109/57.917529; DOI 10.1109/57.917529; File: 03_Data/raw/iec_tc10_duval2001_full/iec_tc10_faulty_equipment.csv; SHA-256 EF9F6B542821264A... |
| DF2 | Made in Step 9 from DS1-DS5 (Steps 5-9 programs). Use: All clean records with role, class, flags and original values. | File: 03_Data/processed/dga_master.csv; SHA-256 AE9E6C0C84CF7180... |
| DF3 | Made in Step 10 from DF2. Use: Fold number of every training record in each of 10 repeats. | File: 03_Data/processed/folds.csv; SHA-256 0CE7D9AF3C7CE9F6... |
| DF6 | Made in Step 13 from all frozen files. Use: SHA-256 of every frozen file; checked by verify_data_version() before every later step. | File: 03_Data/data_version_1.0.sha256; SHA-256 260EBE0C8921E52C... |
| DF20 | Written in Step 19. Use: Feature builder (F1-F4), imputation, scaling, class weights and the six classifiers. | File: 06_Python_ML/src/ml/pipelines.py; SHA-256 8A7131A059C7BDED... |
| DF23 | Produced in Step 21 by step21_select_model.py from DF21, applying the Analysis Plan rule with decision D18. Use: Corrected resampled t-test of every candidate against the best; the chosen pipeline (Random Forest, F4). | File: 07_Experiments/model_selection_tests.csv; SHA-256 49B632867E5F190D... |
| DF24 | Produced in Step 22 by step22_final_fit.py: Random Forest on F4 tuned and fitted on all 439 development records (decision D19). Use: The fitted model used for every test prediction; saved before any test record was predicted. | File: 07_Experiments/2026-10-12_final_fit/final_pipeline.joblib; SHA-256 1C46D10391429385... |
| DF25 | Produced in Step 22 by step22_final_fit.py with DF24; test sets predicted once (see test_set_access.log). Use: Predicted class and class probabilities for every internal-test, IEC TC 10 and Li 2019 record. | File: 11_Results/ml/ml_predictions.csv; SHA-256 D103E8CA1B21C49A... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 12. How this helps the next steps

Next step: Step 23: explain the fitted model with permutation importance and SHAP values (Analysis Plan Section 8.1), reporting the results as found.

•  Step 23 explains the fitted model (permutation importance and SHAP) using these predictions.

•  Step 24 saves the versioned model (dga_model_v1.joblib) and checks that reloading it reproduces ml_predictions.csv exactly.

•  Steps 28 to 30 join these predictions with the conventional ones and give the formal measures, confidence intervals and significance tests.

# 13. Open items and limitations

•  These are first-look point estimates on small sets (58 to 86 records): one record can move macro-F1 by several points; confidence intervals follow in Step 29.

•  No comparison with the conventional methods is made here. On the IEC TC 10 benchmark the conventional methods have a 'home advantage': the IEC ratio limits were refined using these cases (Duval and dePablo, 2001).

•  The development labels come from a source whose labelling method is not documented (decision D7); the lower scores on IEC TC 10 and Li 2019 may partly reflect differences in labelling practice as well as dataset shift.

# 14. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| D2 | discharges of high energy | Arcing with power follow-through: extensive carbonisation, metal fusion, sometimes tripping of the equipment. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| T2 | thermal fault 300 to 700 °C | Overheating in which the paper has carbonised. |
| T3 | thermal fault above 700 °C | Very hot fault: carbonised oil, metal colouring (800 °C) or metal fusion (above 1 000 °C). |
| T12 | T1 or T2 (merged class) | Used in this project when a source does not say whether the thermal fault was below or above 300 °C. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| IEEE | Institute of Electrical and Electronics Engineers | A professional body that publishes engineering standards and journals. |
| Random Forest | random forest | Many decision trees, each trained on a random sample; they vote for the answer. |
| SHAP | SHapley Additive exPlanations | Shows how much each gas pushed a model's decision towards or away from each fault. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Internal test set | Dissanayake unseen test file | 70 records (61 independent of the benchmark) kept away from training. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| Label map | translation table of fault labels | Lists every original label, its new code and the reason. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Cross-validation | repeated train-and-test on parts of the training data | The data are split into parts; each part is used once for testing while the others train the model. |
| Fold | one part of the cross-validation split | Here the training data are cut into 5 folds (parts). |
| Stratified group k-fold | splitting method | Every part has the same mix of fault classes, and near-identical records stay together in one part. |
| Random seed | starting number for the random shuffle | Recording it means the same split can be made again exactly (seed 20261010). |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| D1-D18 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |
| Dual answer (D1/D2) | Two classes returned together | Sometimes the IEC table fits two fault types at once. The method then answers with both (D1/D2); it counts as correct if the true class is either one. |
| Pipeline | chain of processing steps and a model | Feature building, imputation, scaling and the classifier joined so that they are always fitted together on the same training rows. |
| Feature set (F1-F4) | the inputs given to a model | F1 log gases, F2 gas percentages, F3 log-ratios and Duval percentages, F4 all of them (Analysis Plan 5.1). |
| Imputation | filling in an undefined value | An undefined Duval percentage is replaced by the median of the training fold (decision D15). |
| Class weight | importance given to each record in training | w_c = N/(K n_c): rare classes get more weight so that every class counts equally (Analysis Plan Eq. 14). |
| Nested cross-validation | cross-validation inside cross-validation | The inner loop chooses the settings, the outer loop measures performance on data the tuning never saw. |
| Hyperparameter grid | list of settings tried for a model | For example C and gamma of the SVM; the best combination is chosen in the inner loop (Analysis Plan 5.2). |
| Macro-F1 | average F1 score over the classes | The primary performance measure; every class counts equally however rare it is. |
| SD | standard deviation | How much the 50 fold values spread around their mean; a small SD means the result is stable from fold to fold. |
| Balanced accuracy | mean of the per-class recalls | The share of each class that is found, averaged over the classes, so a rare class counts as much as a common one. |
| Kappa | Cohen's kappa | Agreement between predicted and true classes after removing the agreement expected by chance: 0 = chance, 1 = perfect. |
| Corrected resampled t-test | test for two models compared on the same folds | A t-test whose variance is enlarged because cross-validation folds share training records (Nadeau and Bengio, 2003; Analysis Plan Eq. 28). |
| Confusion matrix | table of true against predicted classes | Each row is a true class, each column a predicted class; the diagonal holds the correct answers, every other cell a particular mistake. |
| Dataset shift | test data differ from training data | Records from another laboratory, country or labelling practice can follow a different pattern, so a model usually scores lower on them than in cross-validation. |
| Class probability | model's confidence in each class | For every record the model gives a probability for each of the seven classes; they add up to 1 and the largest is the prediction. |
| joblib | Python file format for saved models | Stores the fitted pipeline (preprocessing and model together) so it can be reloaded and give exactly the same predictions. |