Step 25 Report

Retrain on every gas subset

Environment: Claude Code (this chat)   |   Completed: 12 October 2026   |   Report version 1 (12 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The selected model was retrained and tested by cross-validation for all 31 combinations of the five gases (1550 runs, identical folds). With all five gases the mean macro-F1 is 0.850. The best single gas is C2H4 (0.384); the best pair C2H6+C2H4 (0.584); the best three gases C2H6+C2H4+C2H2 (0.733); the best four H2+C2H6+C2H4+C2H2 (0.833). The smallest combination whose mean loss is at most 0.05 has 4 gases (H2+C2H6+C2H4+C2H2). The formal minimum panel, with the 95 % interval of the loss, is decided in Step 27.

# 1. Purpose of this step

This step answers a practical question for utilities: how much diagnostic ability is lost when fewer than five gases are measured, as with many online monitors? It provides the data for the minimum-panel decision of Step 27.

# 2. Method used

## Approach

The selected pipeline (Random Forest on feature set F4) was trained and tested again for every one of the 31 possible combinations of the five gases, as if only those gases had been measured. Everything else stayed the same: the 50 outer folds of Step 10, the inner tuning of Step 20 with the same seeds, and the same search grid.

For a gas combination, the F4 features are built only from the gases available: the log value of each available gas; the percentage of each gas in their total (when at least two gases are available); a gas ratio only when both of its gases are available (Analysis Plan Section 8); and the Duval percentages only when CH4, C2H4 and C2H2 are all available (decision D22). With all five gases this is exactly F4, which was used as a check.

## Why this method

•  Online gas monitors and portable analysers often measure fewer than five gases; the study shows how much diagnostic power is lost when gases are missing - a practical question for utilities choosing monitoring equipment.

•  Keeping the folds, seeds and tuning identical means that any change in score is caused only by the missing gases (a paired design, Analysis Plan Eq. 36).

•  Retraining for each combination is fairer than feeding zeros for missing gases to the full model, which would give misleading inputs.

## Settings and rules

| Setting | Value |
| --- | --- |
| Gas combinations | 31 = 2^5 - 1 (Analysis Plan Eq. 35) |
| Pipeline | Random Forest (500 trees, class weights), F4 restricted to the available gases (D22); 9-point grid |
| Validation | nested: 50 outer folds of folds.csv; inner StratifiedGroupKFold(5), seeds as in Step 20; macro-F1 |
| Tasks | 31 x 50 = 1 550; 7 parallel processes; run time 8 h 37 min |
| Records | 439 development records only |
| Software | Python 3.12.10, scikit-learn 1.9.1 |

## Equations

25-1=31#1

where:

2  –  ^

w  –  a

ΔS=Macro-F1full-Macro-F1S#2

where:

ΔS  –  loss of macro-F1 when only the gases in combination S are available (positive = worse)

Macro-F1full, Macro-F1S  –  macro-F1 with all five gases and with the gases in S, on the same fold

## Tools and programs

•  06_Python_ML/src/ml/step25_reduced_gas.py (subset feature builder, nested runs, summary, checks)

•  tests/test_reduced_gas.py (5 tests: 31 subsets, full panel = F4 exactly, ratio and Duval rules, percentages)

## Method references

[M13] S. Varma and R. Simon, "Bias in error estimation when using cross-validation for model selection," BMC Bioinformatics, vol. 7, art. 91, 2006. doi: 10.1186/1471-2105-7-91

[M15] L. Breiman, "Random Forests," Machine Learning, vol. 45, no. 1, pp. 5-32, 2001. doi: 10.1023/A:1010933404324

# 3. What was done, step by step

1.  Recorded the scope and feature rules as decision D22 before running (scope chosen by the researcher).

2.  Wrote step25_reduced_gas.py with a subset feature builder and five tests (including that five gases give exactly F4).

3.  Ran a 7-task trial: the five-gas results equalled Step 20 to the last digit. The trial folder was then deleted.

4.  Ran all 1 550 tasks in 8 h 37 min and summarised them; the checks below passed.

# 4. What we found

## Best combination for each number of gases

| Gases | Best combination | Features | Macro-F1 mean (SD) | Mean loss vs five gases |
| --- | --- | --- | --- | --- |
| 1 | C2H4 | 1 | 0.384 (0.048) | 0.466 |
| 2 | C2H6+C2H4 | 5 | 0.584 (0.044) | 0.267 |
| 3 | C2H6+C2H4+C2H2 | 9 | 0.733 (0.043) | 0.117 |
| 4 | H2+C2H6+C2H4+C2H2 | 11 | 0.833 (0.037) | 0.017 |
| 5 | H2+CH4+C2H6+C2H4+C2H2 | 18 | 0.850 (0.038) | 0.000 |

## All 31 combinations (mean over 50 folds)

| Gases | Combination | Features | Macro-F1 mean (SD) | Mean loss | Balanced accuracy |
| --- | --- | --- | --- | --- | --- |
| 1 | C2H4 | 1 | 0.384 (0.048) | 0.466 | 0.412 |
| 1 | C2H6 | 1 | 0.277 (0.037) | 0.573 | 0.301 |
| 1 | H2 | 1 | 0.266 (0.040) | 0.584 | 0.297 |
| 1 | CH4 | 1 | 0.246 (0.039) | 0.604 | 0.253 |
| 1 | C2H2 | 1 | 0.236 (0.033) | 0.614 | 0.296 |
| 2 | C2H6+C2H4 | 5 | 0.584 (0.044) | 0.267 | 0.608 |
| 2 | C2H4+C2H2 | 5 | 0.552 (0.045) | 0.298 | 0.558 |
| 2 | H2+C2H4 | 4 | 0.532 (0.045) | 0.318 | 0.549 |
| 2 | H2+CH4 | 5 | 0.496 (0.048) | 0.354 | 0.513 |
| 2 | CH4+C2H4 | 4 | 0.467 (0.049) | 0.384 | 0.497 |
| 2 | C2H6+C2H2 | 5 | 0.441 (0.041) | 0.409 | 0.463 |
| 2 | H2+C2H2 | 4 | 0.437 (0.047) | 0.413 | 0.477 |
| 2 | H2+C2H6 | 4 | 0.435 (0.055) | 0.415 | 0.447 |
| 2 | CH4+C2H2 | 5 | 0.433 (0.039) | 0.417 | 0.447 |
| 2 | CH4+C2H6 | 4 | 0.369 (0.050) | 0.481 | 0.384 |
| 3 | C2H6+C2H4+C2H2 | 9 | 0.733 (0.043) | 0.117 | 0.745 |
| 3 | H2+C2H6+C2H4 | 7 | 0.708 (0.044) | 0.143 | 0.723 |
| 3 | H2+C2H4+C2H2 | 7 | 0.686 (0.043) | 0.164 | 0.694 |
| 3 | H2+CH4+C2H4 | 7 | 0.658 (0.043) | 0.192 | 0.670 |
| 3 | H2+CH4+C2H2 | 8 | 0.633 (0.044) | 0.217 | 0.643 |
| 3 | CH4+C2H4+C2H2 | 11 | 0.615 (0.050) | 0.235 | 0.625 |
| 3 | H2+C2H6+C2H2 | 7 | 0.601 (0.036) | 0.250 | 0.614 |
| 3 | CH4+C2H6+C2H4 | 7 | 0.577 (0.046) | 0.273 | 0.603 |
| 3 | H2+CH4+C2H6 | 7 | 0.573 (0.048) | 0.277 | 0.586 |
| 3 | CH4+C2H6+C2H2 | 8 | 0.521 (0.037) | 0.329 | 0.530 |
| 4 | H2+C2H6+C2H4+C2H2 | 11 | 0.833 (0.037) | 0.017 | 0.841 |
| 4 | H2+CH4+C2H4+C2H2 | 14 | 0.774 (0.045) | 0.076 | 0.777 |
| 4 | H2+CH4+C2H6+C2H4 | 10 | 0.732 (0.045) | 0.118 | 0.746 |
| 4 | CH4+C2H6+C2H4+C2H2 | 15 | 0.722 (0.046) | 0.128 | 0.736 |
| 4 | H2+CH4+C2H6+C2H2 | 11 | 0.702 (0.037) | 0.148 | 0.710 |
| 5 | H2+CH4+C2H6+C2H4+C2H2 | 18 | 0.850 (0.038) | 0.000 | 0.857 |

Mean loss = mean over the 50 folds of (five-gas macro-F1 minus the combination's macro-F1) on the same fold; a negative value means the combination scored higher on average. Lowest result: C2H2 (0.236).

# 5. Checks

| Check | Result |
| --- | --- |
| Data version 1.0 unchanged (SHA-256 manifest) | PASS |
| All 1 550 tasks completed | PASS (1550) |
| Every development record predicted once per repeat and combination | PASS (136090 prediction rows) |
| Every combination used the identical folds of Step 10 | PASS |
| Five-gas run reproduces the Step 20 Random Forest/F4 fold results exactly | PASS |
| Tasks with any warning | 0 |
| Only development records read | PASS - test sets not used |

# 6. Problems and fixes

•  The first summary reported the check 'five-gas run reproduces Step 20' as FAILED, although the means were equal. Cause: the check compared exact values with values re-read from a CSV file, and the default CSV reader can change the last binary digit of a number. Fix: the check now compares the original task files of both runs - scores, chosen settings, predicted classes and every probability - and passes for all 50 folds. No result changed; nothing was re-run.

•  The computer went to sleep for part of the night; the run paused and continued without loss, because every task is saved as soon as it finishes. The run time stated in this report includes that pause.

# 7. Decisions

•  D22: scope - only the selected pipeline is retrained (researcher's choice, to keep the run to hours instead of about 90 hours); feature rules for a gas combination (procedural, following Analysis Plan Section 8).

# 8. Files produced

•  07_Experiments/2026-10-12_reducedgas_v1/: config.yaml, run_info.json, tasks/ (1 550 result and prediction files), fold_metrics.csv, predictions.csv, step25_checks.json

•  11_Results/reduced_gas/: reduced_gas_results.csv, reduced_gas_subsets.csv; 03_Data/interim/step25_report.md

•  06_Python_ML/src/ml/step25_reduced_gas.py; 06_Python_ML/tests/test_reduced_gas.py

# 9. What was achieved

•  All 1550 tasks finished; every development record was predicted once per repeat for every gas combination.

•  All 31 combinations used the identical folds of Step 10, and the five-gas run reproduced the Step 20 results exactly.

•  The cross-validated macro-F1 and its loss against the full panel are available for every gas combination, with every prediction saved for Step 27.

# 10. Record of this step

| Item | Record |
| --- | --- |
| Step | 25 - Retrain on every gas subset |
| Environment | Claude Code (this chat) |
| Completed | 12 October 2026 |
| Status | Done |
| Main inputs | dga_master.csv and folds.csv (data version 1.0); configs/ml_config.yaml; the pipeline chosen in Step 21 |
| Main outputs | 07_Experiments/2026-10-12_reducedgas_v1; 11_Results/reduced_gas/reduced_gas_results.csv and reduced_gas_subsets.csv |
| Checks | complete 1550/1550; identical folds PASS; five-gas run = Step 20 PASS; 0 tasks with warnings |
| Decisions | D22 (scope: researcher; feature rules: procedural) |

# 11. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DF2 | Made in Step 9 from DS1-DS5 (Steps 5-9 programs). Use: All clean records with role, class, flags and original values. | File: 03_Data/processed/dga_master.csv; SHA-256 AE9E6C0C84CF7180... |
| DF3 | Made in Step 10 from DF2. Use: Fold number of every training record in each of 10 repeats. | File: 03_Data/processed/folds.csv; SHA-256 0CE7D9AF3C7CE9F6... |
| DF6 | Made in Step 13 from all frozen files. Use: SHA-256 of every frozen file; checked by verify_data_version() before every later step. | File: 03_Data/data_version_1.0.sha256; SHA-256 260EBE0C8921E52C... |
| DF18 | Written in Step 19 from the Analysis Plan (Sections 5.1-5.4) and decisions D6, D15, D16. Use: Feature sets, preprocessing, models and search grids used in Steps 19-24. | File: 06_Python_ML/configs/ml_config.yaml; SHA-256 C78C864AEC6751F8... |
| DF20 | Written in Step 19. Use: Feature builder (F1-F4), imputation, scaling, class weights and the six classifiers. | File: 06_Python_ML/src/ml/pipelines.py; SHA-256 8A7131A059C7BDED... |
| DF23 | Produced in Step 21 by step21_select_model.py from DF21, applying the Analysis Plan rule with decision D18. Use: Corrected resampled t-test of every candidate against the best; the chosen pipeline (Random Forest, F4). | File: 07_Experiments/model_selection_tests.csv; SHA-256 49B632867E5F190D... |
| DF28 | Produced in Step 25 by step25_reduced_gas.py (run 2026-10-12_reducedgas_v1; decision D22). Use: Cross-validated macro-F1 and mean loss against the five-gas panel for every gas combination. | File: 11_Results/reduced_gas/reduced_gas_results.csv; SHA-256 D6BA6AC101A26298... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 12. How this helps the next steps

Next step: Step 26 (MATLAB): run the three conventional methods with the gases of each combination removed, to show which method can still give a diagnosis.

•  Step 26 (MATLAB) uses reduced_gas_subsets.csv to show which conventional method can still give a diagnosis for each combination.

•  Step 27 computes the loss with its 95 % bootstrap interval and finds the smallest gas panel within the approved tolerance (delta = 0.05), with Table 4.9 and Figures 4.16-4.17.

# 13. Open items and limitations

•  These are cross-validation results on the development data; the reduced-gas models are not tested on the test sets (not part of the roadmap).

•  Only the selected pipeline was retrained (D22); another classifier could lose more or less when gases are missing.

•  Which gas combinations correspond to commercial online monitors must be taken from published sources (TO VERIFY); this is a labelling step only.

•  Missing gases were simulated by removing them; a real monitor may also measure the remaining gases with different accuracy.

# 14. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| CH4 | methane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H4 | ethylene | Hydrocarbon gas favoured above about 500 °C; it rises as thermal faults get hotter. |
| C2H2 | acetylene | Gas that needs at least 800 to 1 200 °C; formed in significant amounts mainly in electrical arcs. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| Random Forest | random forest | Many decision trees, each trained on a random sample; they vote for the answer. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Complete-case | records with all five gases reported | Used only for the sensitivity analysis. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Cross-validation | repeated train-and-test on parts of the training data | The data are split into parts; each part is used once for testing while the others train the model. |
| Fold | one part of the cross-validation split | Here the training data are cut into 5 folds (parts). |
| Stratified group k-fold | splitting method | Every part has the same mix of fault classes, and near-identical records stay together in one part. |
| Random seed | starting number for the random shuffle | Recording it means the same split can be made again exactly (seed 20261010). |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| D1-D18 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| Pipeline | chain of processing steps and a model | Feature building, imputation, scaling and the classifier joined so that they are always fitted together on the same training rows. |
| Feature set (F1-F4) | the inputs given to a model | F1 log gases, F2 gas percentages, F3 log-ratios and Duval percentages, F4 all of them (Analysis Plan 5.1). |
| Imputation | filling in an undefined value | An undefined Duval percentage is replaced by the median of the training fold (decision D15). |
| Class weight | importance given to each record in training | w_c = N/(K n_c): rare classes get more weight so that every class counts equally (Analysis Plan Eq. 14). |
| Nested cross-validation | cross-validation inside cross-validation | The inner loop chooses the settings, the outer loop measures performance on data the tuning never saw. |
| Hyperparameter grid | list of settings tried for a model | For example C and gamma of the SVM; the best combination is chosen in the inner loop (Analysis Plan 5.2). |
| Macro-F1 | average F1 score over the classes | The primary performance measure; every class counts equally however rare it is. |
| SD | standard deviation | How much the 50 fold values spread around their mean; a small SD means the result is stable from fold to fold. |
| Balanced accuracy | mean of the per-class recalls | The share of each class that is found, averaged over the classes, so a rare class counts as much as a common one. |
| Corrected resampled t-test | test for two models compared on the same folds | A t-test whose variance is enlarged because cross-validation folds share training records (Nadeau and Bengio, 2003; Analysis Plan Eq. 28). |
| Gas combination (subset) | a group of the five gases | One of the 31 ways to measure some but not all of H2, CH4, C2H6, C2H4 and C2H2 (Analysis Plan Eq. 35). |
| Reduced-gas study | testing the model with fewer gases | The model is retrained with only some gases available, to see how much accuracy is lost - relevant for monitors that measure fewer gases. |
| Online gas monitor | instrument fitted to a transformer | Measures dissolved gases continuously in service; many measure only some of the five gases. |