Step 26 Report

Conventional methods with gases removed

Environment: Claude Code (this chat), MATLAB through the MCP connection   |   Completed: 12 October 2026   |   Report version 1 (12 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The IEC 60599, Rogers and Duval Triangle 1 methods were run for all 31 combinations of the five gases, as if the other gases had not been measured. IEC 60599 and Rogers need all five gases, so they can diagnose only the full five-gas panel: for the other 30 combinations they answer 'no diagnosis' (ND) for 100 % of the 827 records. Duval Triangle 1 needs CH4, C2H4 and C2H2 and can diagnose 4 of the 31 combinations; for the other 27 it answers ND for 100 % of the records. The smallest reduced panel that the machine-learning model of Step 25 handles with at most 0.05 loss of macro-F1 (H2+C2H6+C2H4+C2H2) cannot be diagnosed by any of the three methods. The five-gas row reproduces the counts of Steps 14-17 exactly, all 10 automatic checks pass and an independent Python program reproduces all 465 rows.

# 1. Purpose of this step

Real monitors often measure fewer than five gases. This step finds out, for every possible set of measured gases, how often each conventional method can still give a diagnosis. It gives the baseline for the comparison with machine learning in Step 27.

# 2. Method used

## Approach

For each of the 31 combinations of the five gases the program pretends that only those gases were measured: the other gases are replaced by NaN, a marker that means 'not measured'. It is not the same as 0 ppm, which means 'measured and not found'.

A conventional method that needs a gas that is not measured gives no diagnosis (ND) for every sample, before any ratio, zone or normality test is looked at. The IEC 60599 and Rogers methods use the ratios CH4/H2, C2H2/C2H4 and C2H4/C2H6, so they need all five gases; Duval Triangle 1 needs CH4, C2H4 and C2H2. A method that has all its gases is run exactly as in Steps 14-17.

The number and share of ND answers is counted for every combination and method over all 827 records and for each data role. A second program, written independently in Python (Step 18 implementation), recomputes the whole table.

## Why this method

•  Many online monitors measure only some of the gases. This step shows, without guessing, for which of them a conventional method can give any diagnosis at all - the baseline against which the reduced-gas machine-learning models of Step 25 are judged.

•  Returning ND instead of a diagnosis calculated from incomplete data is the safe choice: a ratio with a missing gas has no meaning, and a guessed value would make the conventional methods look better or worse than they are.

•  NaN is used for a missing gas because it spreads through every calculation (a ratio or percentage that uses it is also NaN) and cannot be mistaken for a real measurement of 0 ppm (decision D8).

## Settings and rules

| Setting | Value |
| --- | --- |
| Gas combinations | 31 = 2^5 - 1, from reduced_gas_subsets.csv (checked: all different, none empty) |
| Removed gas | NaN (not measured), never 0 ppm |
| Gases needed | IEC 60599 and Rogers: H2, CH4, C2H6, C2H4, C2H2 (derived from R1, R2, R5); Duval: CH4, C2H4, C2H2 |
| Method without its gases | ND for 100 % of the records, decided before any ratio, zone or gate test |
| Method with its gases | as Steps 14-17: decisions D11-D13, upper normality gate |
| Normality gate with a gas missing | never passed (D23 rule 4, proposed); sensitivity: gate on the measured gases only |
| Records and roles | 827 records, data version 1.0; all, development, internal_test, benchmark, external_test |
| Software | MATLAB 25.2.0.2998904 (R2025b) (base MATLAB, no toolbox); Python 3.12.10 |

## Equations

AmS=1  if Rm⊆S,  otherwise 0#1

where:

AmS  –  applicability of method m to gas combination S (1 = the method can diagnose; 0 = it answers ND for every record)

Rm  –  the set of gases that method m needs (IEC 60599 and Rogers: all five; Duval: CH4, C2H4, C2H2)

m  –  method: IEC 60599, Rogers or Duval Triangle 1

S  –  the set of gases that are measured, one of the 31 combinations

sND=nNDn#2

where:

sND  –  share of records with no diagnosis (0 to 1)

nND  –  number of records for which the method answers ND after the normality gate

n  –  number of records in the data role (all = 827)

## Tools and programs

•  04_MATLAB_Conventional/reduced_gas_diagnosis.m (the rule), run_reduced_gas_applicability.m (31 x 3 x 5 table and 10 checks)

•  04_MATLAB_Conventional/tests/TestReducedGas.m (26 tests); the 67 tests of Step 15 were run again (93 tests in all)

•  06_Python_ML/src/conventional/step26_crosscheck.py and tests/test_step26_crosscheck.py (independent check, 4 tests)

•  00_Project_Admin/report_builder/update_register_step26.ps1 (register, glossary)

## Method references

[ST1] IEC 60599:1999+A1:2007, Mineral oil-impregnated electrical equipment in service - Guide to the interpretation of dissolved and free gases analysis, Ed. 2.1. Geneva: IEC, 2007. https://standards.iteh.ai/catalog/standards/iec/31551405-c771-4a06-b021-4c2433c11fb9/iec-60599-1999

[ST5] IEEE Guide for the Interpretation of Gases Generated in Oil-Immersed Transformers, IEEE Std C57.104-2008 (Revision of IEEE Std C57.104-1991). New York: IEEE, published 2 Feb. 2009. https://standards.ieee.org/ieee/C57.104/4030/ [TO VERIFY against a licensed copy. The 2019 edition (Duval Triangle 1, clause 6.2.3) is still not obtained]

[M9] IEEE Standard for Floating-Point Arithmetic, IEEE Std 754-2019, 2019. doi: 10.1109/IEEESTD.2019.8766229

# 3. What was used

•  The 827 records of data version 1.0 (checked with the SHA-256 manifest before the run) and the 31 gas combinations of Step 25 (reduced_gas_subsets.csv).

•  The functions of Steps 14-17, unchanged: no limit, ratio rule or zone was altered (decisions D11-D13 stay in force).

# 4. What was done, step by step

1.  Wrote the rule as decision D23 (rules 1-3 follow the Analysis Plan; rule 4, the normality gate, is proposed and flagged for the researcher).

2.  Added the gases each method needs to conv_config.m, derived from the ratio definitions (no new limit).

3.  Wrote reduced_gas_diagnosis.m (the rule) and run_reduced_gas_applicability.m (the 31 x 3 x 5 table with 10 automatic checks).

4.  Wrote 26 unit tests, including the one the roadmap asks for (one removed gas gives ND for IEC 60599 and Rogers); all 93 MATLAB tests pass.

5.  Wrote an independent Python check (4 tests); it reproduces all 465 rows.

# 5. The rules

•  A removed gas is NaN (not measured), never 0 ppm.

•  A method that needs a removed gas answers ND for every record, decided before any ratio, zone or gate test. IEC 60599 and Rogers need all five gases; Duval needs CH4, C2H4 and C2H2.

•  A method that has all its gases is run exactly as before, with the upper normality gate of Step 14.

•  The normality gate is passed (Normal) only when all five gases are measured and at or below their typical values; with a gas missing it is never passed (D23 rule 4, proposed).

# 6. What we found

## Which method can diagnose which gas combination

| Method | Combinations it can diagnose | Which |
| --- | --- | --- |
| IEC60599 | 1 of 31 | H2+CH4+C2H6+C2H4+C2H2 |
| Rogers | 1 of 31 | H2+CH4+C2H6+C2H4+C2H2 |
| Duval | 4 of 31 | CH4+C2H4+C2H2; H2+CH4+C2H4+C2H2; CH4+C2H6+C2H4+C2H2; H2+CH4+C2H6+C2H4+C2H2 |

In all other combinations the method answers ND for 100 % of the records. All three methods fail in 27 of the 31 combinations (every combination that lacks CH4, C2H4 or C2H2), including every single gas and every pair that does not contain the three Duval gases.

## Duval Triangle 1: the combinations where it can still diagnose

| Gases measured | Gases | Records | ND before gate | ND after gate (primary) | ND, gate on measured gases (sensitivity) |
| --- | --- | --- | --- | --- | --- |
| CH4+C2H4+C2H2 | 3 | 827 | 2 | 2 | 0 |
| H2+CH4+C2H4+C2H2 | 4 | 827 | 2 | 2 | 1 |
| CH4+C2H6+C2H4+C2H2 | 4 | 827 | 2 | 2 | 0 |
| H2+CH4+C2H6+C2H4+C2H2 | 5 | 827 | 2 | 1 | 1 |

Duval gives ND only for records with CH4, C2H4 and C2H2 all equal to 0 ppm (the percentages are then undefined). In the data these are two development records: DISTRAIN_0531 (H2 = 1023.8 ppm, gate not passed) and DISTRAIN_0532 (H2 = 103.9 ppm, gate passed). With all five gases the gate turns the record whose gases are all at or below their typical values into Normal and the other stays ND (1 record). With a gas missing the gate cannot be passed, so both stay ND (2 records). This is the point flagged in the open items.

## The five-gas row reproduces Steps 14-17

| Method | Data role | Records | ND (this step) | ND_final (Steps 14-17) | Share ND |
| --- | --- | --- | --- | --- | --- |
| IEC60599 | all | 827 | 200 | 200 | 24.2 % |
| IEC60599 | development | 439 | 115 | 115 | 26.2 % |
| IEC60599 | internal_test | 70 | 19 | 19 | 27.1 % |
| IEC60599 | benchmark | 117 | 24 | 24 | 20.5 % |
| IEC60599 | external_test | 201 | 42 | 42 | 20.9 % |
| Rogers | all | 827 | 296 | 296 | 35.8 % |
| Rogers | development | 439 | 157 | 157 | 35.8 % |
| Rogers | internal_test | 70 | 28 | 28 | 40.0 % |
| Rogers | benchmark | 117 | 42 | 42 | 35.9 % |
| Rogers | external_test | 201 | 69 | 69 | 34.3 % |
| Duval | all | 827 | 1 | 1 | 0.1 % |
| Duval | development | 439 | 1 | 1 | 0.2 % |
| Duval | internal_test | 70 | 0 | 0 | 0.0 % |
| Duval | benchmark | 117 | 0 | 0 | 0.0 % |
| Duval | external_test | 201 | 0 | 0 | 0.0 % |

## Conventional methods against the machine-learning model on reduced panels

| Gases measured | ML macro-F1 (Step 25) | ML loss | ND IEC | ND Rogers | ND Duval |
| --- | --- | --- | --- | --- | --- |
| H2+CH4+C2H6+C2H4+C2H2 | 0.850 | 0.000 | 24.2 % | 35.8 % | 0.1 % |
| H2+C2H6+C2H4+C2H2 | 0.833 | 0.017 | 100.0 % | 100.0 % | 100.0 % |
| CH4+C2H4+C2H2 | 0.615 | 0.235 | 100.0 % | 100.0 % | 0.2 % |

ML = the Random Forest on feature set F4 restricted to the measured gases, cross-validated on the 439 development records (Step 25); ND shares are over all 827 records. The only reduced panel with a mean loss of at most 0.05 is H2+C2H6+C2H4+C2H2, and none of the three conventional methods can diagnose it. The panel that Duval can use with the fewest gases, CH4+C2H4+C2H2, gives the machine-learning model a macro-F1 of 0.615. These are different data sets and metrics (ND share against cross-validated macro-F1); the formal comparison with confidence intervals is in Steps 28-30.

# 7. Checks

| Check | Result |
| --- | --- |
| subsets: every non-empty combination once (2^5 - 1 = 31), all different | PASS |
| subsets: none empty, n_gases = number of gases kept | PASS |
| subsets: subset_id matches the gases kept | PASS |
| not applicable -> ND for 100 % of records (all roles) | PASS |
| applicability agrees with iec_rogers_applicable / duval_available of Step 25 | PASS |
| five-gas row reproduces conventional_counts.csv (ND_final, 3 methods x 5 roles) | PASS |
| Duval with CH4, C2H4, C2H2 kept: ND = five-gas Duval ND_raw (all roles) | PASS |
| no "Normal" result when a gas is missing | PASS |
| table: combinations x methods x roles rows, shares in [0,1], n_nd + n_diagnosed = n_records | PASS |
| role sizes add up (the four roles sum to the number of records = all) | PASS |
| Unit tests (MATLAB): old 67 + new 26 | PASS (93 of 93) |
| Audit: no typed limits in the decision code | PASS (0 literals) |
| Independent Python implementation reproduces the table | PASS (465 of 465 rows) |

# 8. Problems and fixes

•  Alert - roadmap check worded loosely: 'for a combination that keeps CH4, C2H4 and C2H2 the Duval ND count equals the five-gas Duval ND count'. The five-gas count after the gate is 1 record, before the gate 2. With a gas missing the gate cannot be passed, so the reduced combinations give 2, which equals the five-gas count before the gate. The check was therefore written against the count before the gate, and both numbers are shown. The alternative rule (gate on the measured gases) is given as a sensitivity column. The choice needs the researcher's confirmation (D23 rule 4).

•  The first test run had two failures: the audit 'no typed limits' found the number 11 in the new batch program (the number of columns of a work table). It was not a limit, but the audit rule is strict, so the line was changed and the audit and all tests pass.

•  The system Python has no numpy; the check program was run with the project's own environment (06_Python_ML/.venv), as in the earlier steps.

•  While updating the results manifest, 11_Results/manifest.csv was found to contain unquoted commas in the four Duval figure rows (they are read with five fields). This was an earlier mistake and is repaired in this session; no result was affected. The manifest also lists only some of the results (it was not kept up to date after Step 17); completing it is an open item.

•  The test log 04_MATLAB_Conventional/tests/test_log.txt, which is register entry DF13 and was the 67-test log of Step 15, was overwritten by this step's run of both test classes (93 tests, all passed). The register entry was updated; the 67-test log itself is not kept.

•  The Word version of the Data and Source Register had not been updated since Step 17 and contained a typing error (66 of 66 tests instead of 67 of 67). It was rebuilt as version 4 and now lists the files of Steps 18 to 26.

•  Earlier in the same session (not part of Step 26) the Simulink model of the rerun folder was found to depend on the MATLAB path: its start-up callbacks only called params_transformer, which lives two folders higher. The callbacks now add that folder to the path (backup kept; recorded in CHANGELOG.md). It is not confirmed that this was the error the researcher saw; the exact error text is still needed.

# 9. Where the standards limits can be verified

Every decision limit used by the three methods is read from a table in 02_Standards; none is typed in the code. All of them are still marked TO VERIFY. The table below says which printed table each file was copied from and where to obtain the document. A correction found at any of these places creates data version 1.1, and Steps 14 to 17 and this step are then re-run (all are automatic).

| Project file | Printed source to compare with | Where to obtain it |
| --- | --- | --- |
| 02_Standards/iec_ratio_table.csv (IEC ratio method, ratios R1, R2, R5) | IEC 60599 Ed. 2.1 (2007), Table 2, p. 11 (read in the official preview). To check: Table 1 of the 2022 edition (p. 14). | IEC 60599:2022 full text, IEC webstore (CHF 260 at the time of reading), or the UMaT library / supervisor |
| 02_Standards/iec_typical_values.csv (normality gate) | IEC 60599 Amendment 1 (2007), Table A.2 (p. 3 of the preview), with its Annex A warning. To check: Table A.2 of the 2022 edition (p. 26). | As above |
| 02_Standards/duval_triangle_zones.csv (Duval Triangle 1) | IEC 60599:2022, Figure B.3 (p. 37 of the preview) and IEEE Std C57.104-2019, clause 6.2.3. Currently taken from a secondary source (Moser 2025, citing C57.104-2019), which agrees with Manisha et al. 2022 and reproduces all 39 printed worked examples. | IEC 60599:2022 and IEEE Std C57.104-2019 (IEEE Xplore, through the UMaT library) |
| 02_Standards/rogers_ratio_table.csv (Rogers ratio method) | IEEE Std C57.104-2008, Table 6 (p. 16) and the worked example of Figure 2 (p. 7). The copy used was not licensed to the project. | IEEE Std C57.104-2008 from a licensed copy (IEEE Xplore, UMaT library) |
| 02_Standards/ieee_condition1_limits.csv | IEEE Std C57.104-2008, Table 1 (p. 10). | As above |

Each file also has a record of what was compared in 02_Standards/sources.md and 02_Standards/transcription_check.md. A corrected limit could change the diagnoses of Steps 14 to 17 and therefore the ND counts in this report; the numbers here are valid for data version 1.0 only.

# 10. Decisions

•  D23: removed gas = NaN; a method that needs a removed gas gives ND for every record; a method with its gases runs as before (rules 1-3, closed on the basis of the Analysis Plan Section 8 and the Step 26 instruction). Rule 4: the normality gate is never passed with a gas missing (proposed, awaiting confirmation).

# 11. Files produced

•  11_Results/conventional/conventional_applicability.csv and conventional_applicability_checks.csv

•  08_Statistical_Analysis/cross_language_check_step26.csv

•  04_MATLAB_Conventional/reduced_gas_diagnosis.m, run_reduced_gas_applicability.m, tests/TestReducedGas.m, code_manifest_step26.sha256 (conv_config.m and tests/run_tests_and_log.m were extended); tests/test_log.txt (93 tests)

•  06_Python_ML/src/conventional/step26_crosscheck.py; 06_Python_ML/tests/test_step26_crosscheck.py

# 12. What was achieved

•  The table conventional_applicability.csv has 465 rows (31 gas combinations x 3 methods x 5 data roles) and passed all 10 automatic checks.

•  IEC 60599 and Rogers can give a diagnosis in 1 of the 31 combinations (all five gases); Duval Triangle 1 in 4 (those that keep CH4, C2H4 and C2H2).

•  Where a method needs a gas that is not measured it answers ND for 100 % of the records - never a guess - and the five-gas row reproduces the counts of Steps 14-17 exactly.

•  The independent Python implementation reproduced all 465 rows; 93 MATLAB tests and the Python tests pass.

# 13. Record of this step

| Item | Record |
| --- | --- |
| Step | 26 - Conventional methods with gases removed |
| Environment | Claude Code (this chat) through the MATLAB MCP connection (D14) |
| Completed | 12 October 2026 |
| Status | Done (rule 4 of D23 awaits the researcher's confirmation) |
| Main inputs | dga_master.csv (data version 1.0, verified); reduced_gas_subsets.csv (Step 25); the functions of Steps 14-17 |
| Main outputs | 11_Results/conventional/conventional_applicability.csv and conventional_applicability_checks.csv; 08_Statistical_Analysis/cross_language_check_step26.csv |
| Checks | 10 of 10 automatic checks PASS; 93 MATLAB tests PASS; Python 4 tests PASS; MATLAB = Python on 465 of 465 rows |
| Decisions | D23 (rules 1-3 closed; rule 4, the normality gate on incomplete data, proposed) |

# 14. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DF2 | Made in Step 9 from DS1-DS5 (Steps 5-9 programs). Use: All clean records with role, class, flags and original values. | File: 03_Data/processed/dga_master.csv; SHA-256 AE9E6C0C84CF7180... |
| DF6 | Made in Step 13 from all frozen files. Use: SHA-256 of every frozen file; checked by verify_data_version() before every later step. | File: 03_Data/data_version_1.0.sha256; SHA-256 260EBE0C8921E52C... |
| DF8 | Made in Steps 14-17: 22 MATLAB files in 04_MATLAB_Conventional and its tests folder. Use: The three conventional methods, boundary distances, tests, batch run, figures. | File: 04_MATLAB_Conventional/code_manifest.sha256; SHA-256 01055ECB9487CE67... |
| DF10 | Made in Step 16 by run_conventional_batch.m. Use: Table of unresolved and dual results. | File: 11_Results/conventional/conventional_counts.csv; SHA-256 0467416EBE509875... |
| DF28 | Produced in Step 25 by step25_reduced_gas.py (run 2026-10-12_reducedgas_v1; decision D22). Use: Cross-validated macro-F1 and mean loss against the five-gas panel for every gas combination. | File: 11_Results/reduced_gas/reduced_gas_results.csv; SHA-256 D6BA6AC101A26298... |
| DF29 | Produced in Step 26 by run_reduced_gas_applicability.m (decision D23): share of ND per gas combination, method and data role. Use: Shows which conventional method can still give a diagnosis when gases are not measured; input of Step 27 comparison. | File: 11_Results/conventional/conventional_applicability.csv; SHA-256 BBF05021D951CC65... |
| DF30 | Produced in Step 26 by run_reduced_gas_applicability.m: the 10 checks of the roadmap and of the input file. Use: Evidence that the table is correct (five-gas row = Steps 14-17, ND = 100 % where a gas is needed). | File: 11_Results/conventional/conventional_applicability_checks.csv; SHA-256 ED620321EF96B800... |
| DF31 | Produced in Step 26 by step26_crosscheck.py: every row of DF29 recomputed with the independent Python implementation of Step 18. Use: Independent check of DF29 (identical on 465 of 465 rows). | File: 08_Statistical_Analysis/cross_language_check_step26.csv; SHA-256 CA94D48E42FB33D9... |
| DF32 | Code written or changed in Step 26: reduced_gas_diagnosis.m, run_reduced_gas_applicability.m, tests/TestReducedGas.m, conv_config.m (new fields only), tests/run_tests_and_log.m, step26_crosscheck.py, test_step26_crosscheck.py. Use: Fingerprints of the Step 26 code; code_manifest.sha256 (DF8) stays the record of Steps 14-17. | File: 04_MATLAB_Conventional/code_manifest_step26.sha256; SHA-256 FF95C12806FB5133... |
| ST1 | IEC 60599:1999+A1:2007, Mineral oil-impregnated electrical equipment in service - Guide to the interpretation of dissolved and free gases analysis, Ed. 2.1. Geneva: IEC, 2007. Use: Primary source of the IEC ratio table (Table 2, p.11) and simplified scheme (Table 3, p.12); fault definitions (5.2). | https://standards.iteh.ai/catalog/standards/iec/31551405-c771-4a06-b021-4c2433c11fb9/iec-60599-1999; File: 02_Standards/iec_ratio_table.csv |
| ST5 | IEEE Guide for the Interpretation of Gases Generated in Oil-Immersed Transformers, IEEE Std C57.104-2008 (Revision of IEEE Std C57.104-1991). New York: IEEE, published 2 Feb. 2009. Use: Rogers ratio table (Table 6, p.16); Condition 1 limits (Table 1, p.10); Rogers worked example (Figure 2, p.7). | https://standards.ieee.org/ieee/C57.104/4030/; File: 02_Standards/rogers_ratio_table.csv; 02_Standards/ieee_condition1_limits.csv |
| M9 | IEEE Standard for Floating-Point Arithmetic, IEEE Std 754-2019, 2019. Use: Basis for comparing a ratio exactly with a printed limit: a correctly rounded quotient equal to a limit gives the same double number. | https://doi.org/10.1109/IEEESTD.2019.8766229; DOI 10.1109/IEEESTD.2019.8766229 |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |
| SW2 | MATLAB R2025b, version 25.2.0.2998904, The MathWorks, Inc., Natick, MA, USA. Use: Runs the conventional-method functions, unit tests, batch run and Duval figures (Steps 14-17). | https://www.mathworks.com/products/matlab.html |

# 15. How this helps the next steps

Next step: Step 27 (Claude Code): the loss of each gas combination with its 95 % bootstrap interval, the smallest panel within the tolerance of 0.05, Table 4.9 and Figures 4.16-4.17.

•  Step 27 compares the reduced-gas machine-learning models with the conventional methods: a method that is not applicable to a gas combination counts as ND there, and the table gives the shares directly.

•  The smallest panel that loses at most 0.05 macro-F1 in Step 25 (H2+C2H6+C2H4+C2H2) is not usable by any conventional method (IEC60599, Rogers, Duval are all not applicable); this is a central argument of the thesis for machine learning with reduced gases.

# 16. Open items and limitations

•  D23 rule 4 (the normality gate is never passed when a gas is missing) is Claude's recommendation and is awaiting the researcher's confirmation. The alternative is reported in the column n_nd_gate_measured; it changes only the Duval counts (a few samples with all measured gases low become Normal instead of ND).

•  The roadmap check 'Duval ND equals the five-gas Duval ND' holds against the count before the gate (2 records), not after it (1 record): with a gas missing the gate cannot declare Normal, so the one record that the five-gas gate turned into Normal stays ND. Reported openly, not hidden.

•  The standards limits behind the three methods are still TO VERIFY against licensed sources (see Steps 12 and 14); a correction would create data version 1.1 and this table would be re-run.

•  11_Results/manifest.csv lists only some of the results (not kept up to date after Step 17); it must be completed.

•  The Simulink start-up callbacks were changed earlier in this session (path fix); the exact error the researcher saw has still not been supplied, so it is not confirmed that this was the error.

•  The counts per data role use all records of the role; the primary benchmark subset (58 power transformers) is not separated here.

•  Which gas combinations correspond to real online monitors is still to be taken from published sources (TO VERIFY).

# 17. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| CH4 | methane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H6 | ethane | Hydrocarbon gas formed when oil is overheated, mainly at the lower fault temperatures. |
| C2H4 | ethylene | Hydrocarbon gas favoured above about 500 °C; it rises as thermal faults get hotter. |
| C2H2 | acetylene | Gas that needs at least 800 to 1 200 °C; formed in significant amounts mainly in electrical arcs. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEEE | Institute of Electrical and Electronics Engineers | A professional body that publishes engineering standards and journals. |
| IEEE C57.104 | IEEE guide for the interpretation of gases generated in oil-immersed transformers | The IEEE standard that contains the Duval Triangle 1 (2019 edition) and the Rogers ratio table (2008 edition). |
| Ratio method | diagnosis from gas ratios | Divides one gas by another (for example C2H2/C2H4) and compares the result with fixed limits to name the fault. |
| Duval Triangle 1 | graphical DGA method by M. Duval | The shares of CH4, C2H4 and C2H2 are plotted as one point in a triangle divided into fault zones. |
| Rogers ratios | older gas-ratio method by R.R. Rogers | A ratio table that names faults from three gas ratios; kept in IEEE C57.104. |
| Typical values | 90 % typical gas concentrations | Levels below which about 90 % of transformers in service are found; not limit values. |
| Normality gate | rule that lets conventional methods answer 'Normal' | If all gases are below their typical values, the conventional methods give Normal instead of a fault (decision D3). |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Random Forest | random forest | Many decision trees, each trained on a random sample; they vote for the answer. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| Complete-case | records with all five gases reported | Used only for the sensitivity analysis. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| venv | virtual environment | A private copy of Python and its libraries that belongs to this project only. |
| pytest | Python testing tool | Runs the automated checks that prove the data rules hold. |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| Simulink, Simscape | MATLAB's block-diagram modelling tool and its physical-modelling library | Used to model the transformer's operating conditions (Simulink Agentic Toolkit); it never makes gas values. |
| D1-D23 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |
| Primary and secondary source | the original document and a document that quotes it | Values from a secondary source are marked TO VERIFY until checked against the primary source. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| R1, R2, R5 | Rogers gas ratios | R1 = CH4/H2, R2 = C2H2/C2H4, R5 = C2H4/C2H6; the three ratios the Rogers method compares with its table. |
| Condition 1 | IEEE normal-level gas limits | The highest gas levels at which IEEE C57.104 considers a transformer to be operating satisfactorily (e.g. H2 100 ppm, C2H2 1 ppm). |
| ND (no diagnosis) | No diagnosis | The answer of a method when no rule applies or a ratio it needs cannot be calculated. It is a result and is never deleted. |
| Dual answer (D1/D2) | Two classes returned together | Sometimes the IEC table fits two fault types at once. The method then answers with both (D1/D2); it counts as correct if the true class is either one. |
| Boundary distance | Distance to the nearest decision boundary | How far a sample is from the line where the diagnosis would change. A small distance means a small measurement error could change the diagnosis. |
| Raw and final result | Result before and after the normality gate | raw_result is what the method itself says; result is what is left after samples with low gas levels have been called Normal by the gate. |
| Unit test (matlab.unittest) | Automatic test of one small piece of code | A test that feeds a function a known input and checks the answer, so that any later change that breaks the function is noticed at once. |
| IEEE 754 | Floating-point arithmetic standard | The rule that decides how computers round decimal numbers; it makes a division that is exactly equal to a limit give exactly the limit. |
| Feature set (F1-F4) | the inputs given to a model | F1 log gases, F2 gas percentages, F3 log-ratios and Duval percentages, F4 all of them (Analysis Plan 5.1). |
| Macro-F1 | average F1 score over the classes | The primary performance measure; every class counts equally however rare it is. |
| Reduced-gas study | testing the model with fewer gases | The model is retrained with only some gases available, to see how much accuracy is lost - relevant for monitors that measure fewer gases. |
| Online gas monitor | instrument fitted to a transformer | Measures dissolved gases continuously in service; many measure only some of the five gases. |
| NaN (not measured) | Not a Number, used here for a gas that was not measured | A marker for a missing value. It is different from 0 ppm: 0 ppm means the gas was measured and not found, NaN means nobody measured it, so no ratio or percentage can be calculated from it. |
| Applicable (method) | A method that has all the gases it needs | A method is applicable to a gas combination when every gas it uses is measured. IEC 60599 and Rogers need all five gases; Duval Triangle 1 needs CH4, C2H4 and C2H2. If a method is not applicable it answers ND for every sample. |
| Gas combination (subset) | A choice of the gases that are measured | One of the 31 ways to keep at least one of the five gases, as with an online monitor that measures only some gases. |