Step 30 Report

Run the significance tests

Environment: Claude Code (this chat)   |   Completed: 12 October 2026   |   Report version 1 (12 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: On the main benchmark (IEC TC 10, inspected power transformers) the ML model is significantly better only than the Rogers ratios; it is not significantly different from IEC 60599 or the Duval Triangle, and Duval was right more often. Criterion 1 of the research hypothesis is therefore not met on the main benchmark, so the hypothesis is not supported there, whatever Step 31 shows. On the internal and Li 2019 test sets the ML model is significantly better than all three methods with the approved normality gate; without the gate it is no longer significantly better than Duval on Li 2019. Among the classifiers, Random Forest and XGBoost cannot be told apart and both rank above the others.

# 1. Purpose of this step

This step tests which observed differences are larger than chance and judges the research hypothesis by the criteria written before any data were analysed (Analysis Plan Section 2.1).

# 2. Method used

## Approach

Three groups of standard tests, all fixed in the Analysis Plan (Section 7) with the remaining details written down as decision D26 before computing.

Classifiers (cross-validation): the Friedman test ranks the six models in each of the 50 outer folds and tests whether their average ranks differ; the Nemenyi critical difference then shows which pairs differ (Demsar, 2006), drawn as a critical-difference diagram (Figure 4.7).

ML against the conventional methods (test sets): on each test set, Cochran's Q first tests whether the four methods have the same share of correct answers; McNemar's test then compares the ML model with each conventional method on the same records, and the Holm correction keeps the chance of any false positive among the three comparisons at 5 %. The odds ratio b/c is the effect size. The same tests were repeated without the normality gate.

Agreement: Cohen's kappa between every pair of methods and the true label (Table 4.7, Figure 4.11). Finally the research hypothesis was judged by its written criteria 1 and 2 (criterion 3 follows in Step 31).

## Why this method

•  Comparing methods on the same records with paired tests (McNemar, Cochran's Q) uses only the records where they differ, which is the correct and most powerful way for this design.

•  Without the Holm correction, three tests per test set would give a higher than 5 % chance of a false 'significant' result.

•  The Friedman/Nemenyi procedure is the standard recommended for comparing several classifiers on the same folds (Demsar, 2006).

## Settings and rules

| Setting | Value |
| --- | --- |
| Significance level | alpha = 0.05, two-sided; exact p-values reported |
| Friedman | 6 models on feature set F4, 50 outer folds; Nemenyi q_alpha from the studentised range distribution = 2.850; CD = 1.066 |
| McNemar | continuity-corrected chi-square (Eq. 30); exact binomial when b + c < 25 (Eq. 31); Holm within each test set (m = 3) |
| Correct answer | strict scoring of D25 (no diagnosis counts as wrong); upper normality gate; sensitivity without gate |
| Odds ratio | b/c with 95 % CI from the log odds ratio; 0.5 added to b and c only when one of them is 0 |
| Hypothesis | judged on the main benchmark, IEC TC 10 power transformers (approved item 2); internal and Li sets supporting |

## Equations

χF2=12nfkk+1jRj2-kk+124#1

where:

nf, k  –  folds (50) and models (6)

Rj  –  average rank of model j (1 = best)

CD=qαkk+16nf#2

where:

q  –  _

c  –  r

χ2=b-c-12b+c#3

where:

b  –  records the ML model got right and the conventional method got wrong

c  –  records the conventional method got right and the ML model got wrong

## Tools and programs

•  06_Python_ML/src/stats/step30_tests.py (Friedman, Nemenyi, Cochran's Q, McNemar, Holm, kappa, hypothesis criteria, Figures 4.7 and 4.11)

•  tests/test_significance.py (5 tests: McNemar, Holm and Cochran equal statsmodels; Friedman equals scipy; q_alpha equals Demsar's table)

## Method references

[M25] M. Friedman, "The use of ranks to avoid the assumption of normality implicit in the analysis of variance," Journal of the American Statistical Association, vol. 32, no. 200, pp. 675-701, 1937. doi: 10.1080/01621459.1937.10503522

[M26] J. Demsar, "Statistical comparisons of classifiers over multiple data sets," Journal of Machine Learning Research, vol. 7, pp. 1-30, 2006. https://www.jmlr.org/papers/v7/demsar06a.html

[M27] P. B. Nemenyi, Distribution-free multiple comparisons, PhD thesis, Princeton University, 1963.

[M28] W. G. Cochran, "The comparison of percentages in matched samples," Biometrika, vol. 37, pp. 256-266, 1950.

[M29] Q. McNemar, "Note on the sampling error of the difference between correlated proportions or percentages," Psychometrika, vol. 12, no. 2, pp. 153-157, 1947. doi: 10.1007/BF02295996

[M30] S. Holm, "A simple sequentially rejective multiple test procedure," Scandinavian Journal of Statistics, vol. 6, no. 2, pp. 65-70, 1979. https://www.jstor.org/stable/4615733

[M22] J. Cohen, "A coefficient of agreement for nominal scales," Educational and Psychological Measurement, vol. 20, no. 1, pp. 37-46, 1960. doi: 10.1177/001316446002000104

# 3. What was done, step by step

1.  Recorded the researcher's confirmation of decision D23 rule (4), and checked open source details online: Crossref, the DOI registration agency, confirmed four references; Duval (2002) was added to the register, its full text still to be read.

2.  Fixed the test details as decision D26 before computing.

3.  Wrote step30_tests.py and five tests comparing its functions with statsmodels and scipy; ran it; tidied the layout of Figure 4.7 and ran it again with identical results.

# 4. What we found

## Classifiers: Friedman and Nemenyi (50 outer folds, feature set F4)

| Model | Average rank (1 = best) | Mean macro-F1 |
| --- | --- | --- |
| Random Forest | 1.76 | 0.850 |
| XGBoost | 2.28 | 0.842 |
| Logistic regression | 3.42 | 0.820 |
| SVM (RBF) | 3.50 | 0.819 |
| Neural network (MLP) | 4.04 | 0.805 |
| Majority baseline | 6.00 | 0.046 |

Friedman: chi-square = 158.06, df = 5, p < 0.001. Critical difference (Nemenyi, alpha 0.05) = 1.066. Random Forest and XGBoost differ by less than the critical difference and cannot be told apart; Random Forest ranks significantly better than logistic regression, the SVM, the neural network and the baseline. This agrees with Step 21 (corrected resampled t-test, p = 0.621 for Random Forest against XGBoost). Supplementary, over all 24 model-feature combinations: chi-square = 757.56, p < 0.001, CD = 5.14.

Figure 4.7  Critical-difference diagram of the six models (feature set F4, 50 outer folds)

Models joined by a thick bar differ by less than the critical difference and cannot be told apart statistically.

## Cochran's Q: do the four methods differ at all?

| Test set | Gate | Records | Correct: ML / Rogers / IEC / Duval | Q (df 3) | p |
| --- | --- | --- | --- | --- | --- |
| Internal test | with gate | 61 | 50 / 20 / 29 / 34 | 42.20 | < 0.001 |
| Internal test | no gate | 61 | 50 / 22 / 26 / 32 | 37.22 | < 0.001 |
| IEC TC 10 (power transformers) | with gate | 58 | 42 / 28 / 37 / 45 | 21.65 | < 0.001 |
| IEC TC 10 (power transformers) | no gate | 58 | 42 / 31 / 42 / 52 | 26.23 | < 0.001 |
| Li 2019 | with gate | 86 | 54 / 15 / 26 / 39 | 57.24 | < 0.001 |
| Li 2019 | no gate | 86 | 54 / 22 / 38 / 64 | 66.46 | < 0.001 |

On every test set the four methods differ significantly in their share of correct answers, so the pairwise McNemar tests are justified.

## Table 4.6 - ML against each conventional method (McNemar, Holm-adjusted)

### With the approved normality gate (primary)

| Test set | Comparison | b | c | Test | p | p (Holm) | Odds ratio b/c [95 % CI] | Signif. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Internal test | ML vs Rogers Ratio | 33 | 3 | chi2 23.36 | < 0.001 | < 0.001 | 11.00 [3.37, 35.87] | yes |
| Internal test | ML vs IEC 60599 ratio | 24 | 3 | chi2 14.81 | < 0.001 | < 0.001 | 8.00 [2.41, 26.57] | yes |
| Internal test | ML vs Duval Triangle 1 | 22 | 6 | chi2 8.04 | 0.005 | 0.005 | 3.67 [1.49, 9.04] | yes |
| IEC TC 10 (power transformers) | ML vs Rogers Ratio | 17 | 3 | exact | 0.003 | 0.008 | 5.67 [1.66, 19.34] | yes |
| IEC TC 10 (power transformers) | ML vs IEC 60599 ratio | 8 | 3 | exact | 0.227 | 0.453 | 2.67 [0.71, 10.05] | no |
| IEC TC 10 (power transformers) | ML vs Duval Triangle 1 | 6 | 9 | exact | 0.607 | 0.607 | 0.67 [0.24, 1.87] | no |
| Li 2019 | ML vs Rogers Ratio | 41 | 2 | chi2 33.58 | < 0.001 | < 0.001 | 20.50 [4.96, 84.75] | yes |
| Li 2019 | ML vs IEC 60599 ratio | 30 | 2 | chi2 22.78 | < 0.001 | < 0.001 | 15.00 [3.58, 62.77] | yes |
| Li 2019 | ML vs Duval Triangle 1 | 29 | 14 | chi2 4.56 | 0.033 | 0.033 | 2.07 [1.09, 3.92] | yes |

### Sensitivity: without the normality gate

| Test set | Comparison | b | c | Test | p | p (Holm) | Odds ratio b/c [95 % CI] | Signif. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Internal test | ML vs Rogers Ratio | 30 | 2 | chi2 22.78 | < 0.001 | < 0.001 | 15.00 [3.58, 62.77] | yes |
| Internal test | ML vs IEC 60599 ratio | 24 | 0 | exact | < 0.001 | < 0.001 | 49.00 [2.98, 805.79] | yes |
| Internal test | ML vs Duval Triangle 1 | 22 | 4 | chi2 11.12 | < 0.001 | < 0.001 | 5.50 [1.90, 15.96] | yes |
| IEC TC 10 (power transformers) | ML vs Rogers Ratio | 15 | 4 | exact | 0.019 | 0.058 | 3.75 [1.24, 11.30] | no |
| IEC TC 10 (power transformers) | ML vs IEC 60599 ratio | 6 | 6 | exact | 1.000 | 1.000 | 1.00 [0.32, 3.10] | no |
| IEC TC 10 (power transformers) | ML vs Duval Triangle 1 | 3 | 13 | exact | 0.021 | 0.058 | 0.23 [0.07, 0.81] | no |
| Li 2019 | ML vs Rogers Ratio | 34 | 2 | chi2 26.69 | < 0.001 | < 0.001 | 17.00 [4.08, 70.76] | yes |
| Li 2019 | ML vs IEC 60599 ratio | 19 | 3 | exact | < 0.001 | 0.002 | 6.33 [1.87, 21.40] | yes |
| Li 2019 | ML vs Duval Triangle 1 | 8 | 18 | chi2 3.12 | 0.078 | 0.078 | 0.44 [0.19, 1.02] | no |

b: ML right, other method wrong; c: other method right, ML wrong. An odds ratio below 1 means the conventional method was right more often. On IEC TC 10 the conventional methods have a home advantage (IEC 60599 limits refined on these cases).

## Table 4.7 - agreement between methods (Cohen's kappa)

Figure 4.11  Cohen's kappa between the true label and every method, on each test set

Agreement with the true label on IEC TC 10: ML (selected model) 0.60, Rogers Ratio 0.33, IEC 60599 ratio 0.53, Duval Triangle 1 0.69. Verbal labels for kappa are a guide only, never a test (plan Section 7.5).

## The research hypothesis - criteria 1 and 2

| Test set | Criterion 1: ML more accurate, Holm p < 0.05 | Criterion 2: conditional gap smaller than strict gap |
| --- | --- | --- |
| Internal test | Rogers yes, IEC yes, Duval yes -> MET | Rogers yes, IEC yes, Duval no -> NOT MET |
| IEC TC 10 (power transformers) | Rogers yes, IEC no, Duval no -> NOT MET | Rogers yes, IEC yes, Duval no -> NOT MET |
| Li 2019 | Rogers yes, IEC yes, Duval yes -> MET | Rogers yes, IEC yes, Duval no -> NOT MET |

•  Main benchmark (IEC TC 10, decision D26): criterion 1 is not met - the ML model is significantly better than Rogers only; against IEC 60599 the difference is not significant, and Duval was right on more records than the ML model (not significant). By the written rule, the hypothesis is NOT SUPPORTED on the main benchmark, whatever criterion 3 shows.

•  Supporting test sets: on the internal and Li 2019 sets criterion 1 is met with the approved gate. Criterion 2 is met against Rogers and IEC 60599 (part of the ML advantage comes from always answering) but cannot be met against Duval, which always answers, so these sets give partial support.

•  The final verdict, with criterion 3, is stated after Step 31.

# 5. Checks

| Check | Result |
| --- | --- |
| Data version 1.0 and merged file unchanged (SHA-256) | PASS |
| McNemar, Holm, Cochran's Q equal statsmodels; Friedman equals scipy; q_alpha equals Demsar's table (k = 6: 2.850) | PASS |
| Re-run after the figure change: identical results | PASS |
| Text statements checked against the result files by the report builder | PASS |
| Full automated test suite | PASS - 117 of 117 tests pass |

# 6. Problems and fixes

•  Online checks: Crossref returned a wrong record for Holm (1979) and was rate-limited for Cochran (1950); both were confirmed from other records (JSTOR identifier; published reference lists). Cochran's DOI and Nemenyi's thesis details remain TO VERIFY.

•  The primary source needed to settle whether the Duval Triangle zones were tuned on the IEC TC 10 cases (Duval 2002) is behind a subscription; it was added to the register as TO VERIFY.

# 7. Decisions

•  D26 (procedural): models in the Friedman test, McNemar and Holm details, odds-ratio correction, kappa categories, main benchmark for the verdict.

•  D23 rule (4) confirmed by the researcher: a sample with a missing gas is never declared Normal by the gate.

# 8. Files produced

•  08_Statistical_Analysis/: cochran_mcnemar.csv, cochran_q.csv, friedman.csv, friedman_ranks_F4.csv, nemenyi_pairs.csv, kappa_matrix.csv, hypothesis_criteria.json

•  11_Results/tables/T4_6_mcnemar.csv, T4_7_kappa.csv; 11_Results/figures/F4_7_critical_difference, F4_11_kappa_agreement (PNG, PDF, CSV)

•  06_Python_ML/src/stats/step30_tests.py; 06_Python_ML/tests/test_significance.py; 03_Data/interim/step30_report.md

# 9. What was achieved

•  All planned significance tests are computed with exact p-values and effect sizes, significant or not.

•  The research hypothesis has been judged by its written criteria 1 and 2; the verdict on the main benchmark is already determined by criterion 1.

•  Tables 4.6 and 4.7 and Figures 4.7 and 4.11 are produced with their data files.

# 10. Record of this step

| Item | Record |
| --- | --- |
| Step | 30 - Run the significance tests |
| Environment | Claude Code (this chat) |
| Completed | 12 October 2026 |
| Status | Done |
| Main inputs | 07_Experiments/2026-10-11_nestedcv_v1/fold_metrics.csv; 08_Statistical_Analysis/merged_predictions.csv |
| Main outputs | 08_Statistical_Analysis/ (cochran_mcnemar.csv, cochran_q.csv, friedman.csv, nemenyi_pairs.csv, kappa_matrix.csv, hypothesis_criteria.json); Tables T4_6, T4_7; Figures F4_7, F4_11 |
| Checks | test functions equal statsmodels/scipy; re-run identical; 117 of 117 tests pass |
| Decisions | D26 (test details; procedural); D23 rule (4) confirmed by the researcher |

# 11. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DF21 | Produced in Step 20 by step20_nested_cv.py (run 2026-10-11_nestedcv_v1, 21:01-23:44, 6 workers). Use: Chosen setting, inner score and all Section 6 measures of every outer-fold task (6 models x 4 feature sets x 50 folds). | File: 07_Experiments/2026-10-11_nestedcv_v1/fold_metrics.csv; SHA-256 5215981A5636EF1E... |
| DF34 | Produced in Step 28 by step28_merge_predictions.py from DF2, DF9 (conventional predictions) and DF25 (ML predictions). Use: True class, flags, ML prediction and probabilities, conventional answers (raw, upper gate, lower gate, merged classes), boundary distances. | File: 08_Statistical_Analysis/merged_predictions.csv; SHA-256 EDB799A2CDA41A69... |
| DF35 | Produced in Step 29 by step29_measures.py from DF34 only (decision D25). Use: Strict and conditional accuracy, coverage (Wilson), macro-F1, balanced accuracy, kappa, MCC (bootstrap) for every method and set. | File: 08_Statistical_Analysis/performance_measures.csv; SHA-256 C86B438A3EF7873F... |
| DF37 | Produced in Step 30 by step30_tests.py from DF21 (fold results) and DF34 (merged predictions); decision D26. Use: McNemar (Holm), Cochran's Q, Friedman/Nemenyi, kappa, hypothesis criteria. | File: 08_Statistical_Analysis/cochran_mcnemar.csv; SHA-256 CCC3414122D688BB... |
| DF38 | Produced in Step 30 by step30_tests.py. Use: McNemar tests with Holm correction and odds ratios; kappa between all methods. | File: 11_Results/tables/T4_6_mcnemar.csv; SHA-256 68967DAAD7983D8C... |
| DS1 | M. Duval and A. dePablo, "Interpretation of gas-in-oil analysis using new IEC publication 60599 and IEC TC 10 databases," IEEE Electrical Insulation Magazine, vol. 17, no. 2, pp. 31-41, Mar./Apr. 2001. Use: Main benchmark (labels confirmed by inspection): primary analysis = 58 power transformers (codes P, U); sensitivity = all 117. | https://doi.org/10.1109/57.917529; DOI 10.1109/57.917529; File: 03_Data/raw/iec_tc10_duval2001_full/iec_tc10_faulty_equipment.csv; SHA-256 EF9F6B542821264A... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 12. How this helps the next steps

Next step: Step 31: fit the logistic regression of disagreement (ML different from each conventional method) on the distance to the nearest decision boundary, to decide criterion 3 and complete the verdict.

•  Step 31 tests criterion 3 (are disagreements concentrated near the decision boundaries?) and completes the verdict.

•  Step 32 builds all Chapter 4 tables and figures from these files, including Figures 4.6, 4.9 and 4.10.

# 13. Open items and limitations

•  The Friedman/Nemenyi tests use 50 folds of one data set, which are not independent; they support, but do not replace, the corrected resampled t-test of Step 21.

•  With 58 records the IEC TC 10 test has limited power: 'not significant' there means the data cannot separate the methods, not that they are equal.

•  Criterion 2 cannot be met against Duval as written, because Duval always gives a diagnosis (its strict and conditional gaps are equal); this is reported, not reinterpreted.

•  Home advantage of the conventional methods on IEC TC 10 (IEC limits refined on these cases); whether the Duval zones were also tuned on them remains TO VERIFY from Duval (2002), register M24.

# 14. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| IEEE | Institute of Electrical and Electronics Engineers | A professional body that publishes engineering standards and journals. |
| Duval Triangle 1 | graphical DGA method by M. Duval | The shares of CH4, C2H4 and C2H2 are plotted as one point in a triangle divided into fault zones. |
| Rogers ratios | older gas-ratio method by R.R. Rogers | A ratio table that names faults from three gas ratios; kept in IEEE C57.104. |
| Normality gate | rule that lets conventional methods answer 'Normal' | If all gases are below their typical values, the conventional methods give Normal instead of a fault (decision D3). |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| SVM | support vector machine | A classifier that separates classes with the widest possible boundary. |
| Random Forest | random forest | Many decision trees, each trained on a random sample; they vote for the answer. |
| XGBoost | extreme gradient boosting | Decision trees built one after another, each correcting the errors of the previous ones. |
| MLP | multilayer perceptron | A small artificial neural network with layers of connected units. |
| Logistic regression | multinomial logistic regression | A simple, explainable model that turns weighted gas values into class probabilities. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| Internal test set | Dissanayake unseen test file | 70 records (61 independent of the benchmark) kept away from training. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Cross-validation | repeated train-and-test on parts of the training data | The data are split into parts; each part is used once for testing while the others train the model. |
| Fold | one part of the cross-validation split | Here the training data are cut into 5 folds (parts). |
| p-value | probability value | The chance of seeing differences at least this large if there were really no difference; very small means a real difference. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| PNG, PDF, dpi | image file, printable document file, dots per inch | Figures are saved as PNG at 300 dpi (sharp for printing) and as PDF. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| venv | virtual environment | A private copy of Python and its libraries that belongs to this project only. |
| pytest | Python testing tool | Runs the automated checks that prove the data rules hold. |
| D1-D23 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| ND (no diagnosis) | No diagnosis | The answer of a method when no rule applies or a ratio it needs cannot be calculated. It is a result and is never deleted. |
| Boundary distance | Distance to the nearest decision boundary | How far a sample is from the line where the diagnosis would change. A small distance means a small measurement error could change the diagnosis. |
| Feature set (F1-F4) | the inputs given to a model | F1 log gases, F2 gas percentages, F3 log-ratios and Duval percentages, F4 all of them (Analysis Plan 5.1). |
| Nested cross-validation | cross-validation inside cross-validation | The inner loop chooses the settings, the outer loop measures performance on data the tuning never saw. |
| Macro-F1 | average F1 score over the classes | The primary performance measure; every class counts equally however rare it is. |
| Balanced accuracy | mean of the per-class recalls | The share of each class that is found, averaged over the classes, so a rare class counts as much as a common one. |
| Kappa | Cohen's kappa | Agreement between predicted and true classes after removing the agreement expected by chance: 0 = chance, 1 = perfect. |
| MCC | Matthews correlation coefficient | One score from -1 to 1 that uses the whole confusion matrix; 0 means no better than guessing. |
| Corrected resampled t-test | test for two models compared on the same folds | A t-test whose variance is enlarged because cross-validation folds share training records (Nadeau and Bengio, 2003; Analysis Plan Eq. 28). |
| Friedman and Nemenyi tests | rank-based comparison of several models | Friedman tests whether models' average ranks over the folds differ; Nemenyi then shows which pairs differ (Step 30). |
| Majority baseline | reference model | Always predicts the most common class; any useful model must do clearly better. |
| Average rank | mean position among the compared models | In every fold the models are ranked by macro-F1 (1 = best); the ranks are then averaged over the folds. |
| RBF | radial basis function | The kernel that lets the SVM draw curved boundaries between classes. |
| Class probability | model's confidence in each class | For every record the model gives a probability for each of the seven classes; they add up to 1 and the largest is the prediction. |
| Bootstrap (stratified percentile) | resampling to get a confidence interval | The records are drawn again at random, with replacement and within each fault class, 2000 times; the middle 95 % of the recomputed values is the 95 % interval (Analysis Plan Section 6.2). |
| Conditional accuracy | correct answers out of the records answered | Looks only at the cases where the method gave a diagnosis (Analysis Plan Eq. 7). |
| Coverage | share of records that get a diagnosis | 1 minus the share of no-diagnosis answers (Analysis Plan Eq. 6); the ML model always answers, so its coverage is 100 %. |
| Wilson interval | confidence interval for a proportion | A 95 % interval for an accuracy or a coverage that works well for small samples (Analysis Plan Eq. 21). |
| Home advantage | benchmark used when the method was built | The IEC 60599 limits were refined with the IEC TC 10 cases, so the conventional methods may score higher on that benchmark than on new data. |
| McNemar test | paired test of two methods on the same records | Uses only the records where one method is right and the other wrong (b and c); tests whether b and c differ more than chance (Analysis Plan Eqs. 30-31). |
| Cochran's Q | test of several methods on the same records | Tests whether all methods have the same share of correct answers before the pairwise tests (Analysis Plan Eq. 29). |
| Holm correction | adjustment for several tests | Keeps the chance of any false positive among the three comparisons per test set at 5 % (Analysis Plan Eq. 32). |
| Critical difference (CD) | smallest significant gap in average rank | Two models whose average ranks differ by less than the CD cannot be told apart (Nemenyi test, Analysis Plan Eq. 27). |
| Odds ratio b/c | effect size of the McNemar test | How many times more often the ML model was right where the other method was wrong than the reverse; 1 = no difference. |