Step 31C Report

Leave-one-source-out training and prediction (Study 2)

Environment: Claude Code (this chat)   |   Completed: 12 October 2026   |   Report version 1 (12 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: All Study 2 models were trained and applied exactly as the protocol specifies: each source held out in turn, models B and C tuned on the other sources only, model A applied unchanged; 24 tuned fits in three variants and 4443 saved predictions. No held-out record or near-copy entered any training set, and re-fitting two tasks from scratch reproduced them exactly. The performance results are computed in Step 31D.

# 1. Purpose of this step

This step produces the Study 2 predictions: for every held-out record, what models A, B and C would have said, with the probability of each class.

# 2. Method used

## Approach

Leave-one-source-out: each of the four sources was held out in turn. Models B (pooled Random Forest on the 18 gas features) and C (hybrid: the same plus the conventional methods' answers, gate flags and boundary distances, 49 inputs) were tuned and fitted on the other three sources only, then predicted the held-out source once. The released model A was applied unchanged to the three external sources.

Tuning repeated the Step 20 procedure inside the training sources: the same 9-point grid, 5-fold grouped cross-validation that keeps near-copies together, macro-F1. Two sensitivity variants were run: equal total weight for each training source, and all 117 IEC TC 10 records instead of the 58 power transformers.

## Why this method

•  Holding out a whole source shows how a model performs on data from a laboratory or database it has never seen - the situation of a utility using the model in practice.

•  Re-using the Step 20 tuning procedure means the only differences from the main study are the training sources and, for model C, the extra inputs.

## Settings and rules

| Setting | Value |
| --- | --- |
| Held-out sources | Dissanayake training, Dissanayake unseen, IEC TC 10 (58 power transformers), Li 2019 |
| Models | A released (unchanged, T1/T2 merged); B pooled RF/F4 (18 inputs); C hybrid (49 inputs) |
| Tuning | GridSearchCV, Step 20 grid (9 settings), StratifiedGroupKFold(5) with pooled near-duplicate groups, macro-F1; balanced class weights |
| Seeds | 20261012 + index of the held-out source |
| Variants | primary; equal source weight; IEC TC 10 all 117 records |
| Software | scikit-learn 1.9.1 |

## Tools and programs

•  06_Python_ML/src/study2/study2_models.py (hybrid features, weighted classifier)

•  06_Python_ML/src/study2/step31c_loso.py (splits, tuning, predictions, rerun check)

•  tests/test_study2_models.py (5 tests incl. leakage-free splits)

## Method references

[M15] L. Breiman, "Random Forests," Machine Learning, vol. 45, no. 1, pp. 5-32, 2001. doi: 10.1023/A:1010933404324

[M13] S. Varma and R. Simon, "Bias in error estimation when using cross-validation for model selection," BMC Bioinformatics, vol. 7, art. 91, 2006. doi: 10.1186/1471-2105-7-91

# 3. What was done, step by step

1.  Wrote study2_models.py (hybrid inputs over fixed answer categories; a class-weighted classifier that can also take source weights) and step31c_loso.py; five tests, including one that checks every split for leakage.

2.  Checked the protocol fingerprint and the Study 2 data manifest at the start of the run, then ran all splits and variants.

3.  Re-fitted two saved tasks from scratch and compared them with the saved predictions.

# 4. What was run

| Variant | Held out | Model | Train | Test | Inputs | Inner macro-F1 | Chosen setting |
| --- | --- | --- | --- | --- | --- | --- | --- |
| primary | Dissanayake training | B | 204 | 439 | 18 | 0.768 | depth=None, leaf=5 |
| primary | Dissanayake training | C | 204 | 439 | 49 | 0.810 | depth=None, leaf=2 |
| primary | Dissanayake unseen | B | 582 | 61 | 18 | 0.862 | depth=None, leaf=2 |
| primary | Dissanayake unseen | C | 582 | 61 | 49 | 0.867 | depth=10, leaf=2 |
| primary | IEC TC 10 | B | 585 | 58 | 18 | 0.866 | depth=None, leaf=1 |
| primary | IEC TC 10 | C | 585 | 58 | 49 | 0.862 | depth=10, leaf=1 |
| primary | Li 2019 | B | 558 | 85 | 18 | 0.881 | depth=None, leaf=2 |
| primary | Li 2019 | C | 558 | 85 | 49 | 0.888 | depth=None, leaf=2 |
| equal source weight | Dissanayake training | B | 204 | 439 | 18 | 0.771 | depth=None, leaf=2 |
| equal source weight | Dissanayake training | C | 204 | 439 | 49 | 0.794 | depth=None, leaf=2 |
| equal source weight | Dissanayake unseen | B | 582 | 61 | 18 | 0.818 | depth=None, leaf=1 |
| equal source weight | Dissanayake unseen | C | 582 | 61 | 49 | 0.831 | depth=10, leaf=1 |
| equal source weight | IEC TC 10 | B | 585 | 58 | 18 | 0.861 | depth=10, leaf=1 |
| equal source weight | IEC TC 10 | C | 585 | 58 | 49 | 0.857 | depth=None, leaf=1 |
| equal source weight | Li 2019 | B | 558 | 85 | 18 | 0.861 | depth=None, leaf=1 |
| equal source weight | Li 2019 | C | 558 | 85 | 49 | 0.870 | depth=10, leaf=1 |
| IEC TC 10 all 117 | Dissanayake training | B | 263 | 439 | 18 | 0.800 | depth=None, leaf=2 |
| IEC TC 10 all 117 | Dissanayake training | C | 263 | 439 | 49 | 0.764 | depth=None, leaf=5 |
| IEC TC 10 all 117 | Dissanayake unseen | B | 641 | 61 | 18 | 0.851 | depth=None, leaf=2 |
| IEC TC 10 all 117 | Dissanayake unseen | C | 641 | 61 | 49 | 0.859 | depth=5, leaf=2 |
| IEC TC 10 all 117 | IEC TC 10 | B | 585 | 117 | 18 | 0.866 | depth=None, leaf=1 |
| IEC TC 10 all 117 | IEC TC 10 | C | 585 | 117 | 49 | 0.862 | depth=10, leaf=1 |
| IEC TC 10 all 117 | Li 2019 | B | 617 | 85 | 18 | 0.870 | depth=None, leaf=2 |
| IEC TC 10 all 117 | Li 2019 | C | 617 | 85 | 49 | 0.886 | depth=None, leaf=1 |

Inner macro-F1 = tuning score on the training sources (not a result). Model A needs no tuning; it is the released model of Step 24.

# 5. Checks

| Check | Result |
| --- | --- |
| Protocol fingerprint and Study 2 data manifest unchanged | PASS |
| No held-out record or near-copy in any training set | PASS |
| Re-fit of two saved tasks gives identical predictions and probabilities | PASS |
| Warnings during fitting | none |
| Full automated test suite | PASS - 130 of 130 |

# 6. Problems and fixes

•  The run took longer than first estimated, and the computer slept for part of it; the run continued without loss and the results are unaffected (seeded and checked by re-fitting).

# 7. Decisions

•  No new decision; protocol D28 applied as written.

# 8. Files produced

•  07_Experiments/2026-10-12_study2_loso/: config.json, fits.json, predictions.csv, rerun_check.json

•  06_Python_ML/src/study2/study2_models.py, step31c_loso.py; 06_Python_ML/tests/test_study2_models.py; 03_Data/interim/step31c_report.md

# 9. What was achieved

•  All 24 tuned fits finished; 4443 predictions with class probabilities are saved.

•  No held-out record or near-copy entered any training set (checked in the program and by tests).

•  Two tasks re-fitted from scratch gave identical predictions and probabilities.

# 10. Record of this step

| Item | Record |
| --- | --- |
| Step | 31C - Leave-one-source-out training and prediction (Study 2) |
| Environment | Claude Code (this chat) |
| Completed | 12 October 2026 |
| Status | Done |
| Main inputs | 03_Data/study2/study2_pooled.csv (manifest checked); ml_config.yaml; dga_model_v1 |
| Main outputs | 07_Experiments/2026-10-12_study2_loso/ (config.json, fits.json, predictions.csv, rerun_check.json) |
| Checks | leakage-free splits; rerun identical; 130 of 130 tests pass |
| Decisions | none new (protocol D28) |

# 11. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DF41 | Produced in Step 31B by step31b_pooled.py from DF2 and DF9 by the rules of the Study 2 protocol (DF40, decision D28). Use: Pooled, deduplicated records of the four sources with six classes, near-duplicate groups and hybrid inputs. | File: 03_Data/study2/study2_pooled.csv; SHA-256 3B03F7D44B56A87B... |
| DF27 | Produced in Step 24 by step24_save_model.py: byte-for-byte copy of DF24 (decision D21). Use: The released model: loaded through model_io.load_model(); reproduces ml_predictions.csv exactly. | File: 06_Python_ML/models/dga_model_v1.joblib; SHA-256 1C46D10391429385... |
| DF40 | Written in Step 31A (decision D28) before any Study 2 model was trained; fingerprint recorded in 03_Data/study2/study2_protocol.sha256. Use: Fixes the questions, data rules, models, measures, statistics and decision rules of Study 2. | File: 00_Project_Admin/Study2_Protocol.docx; SHA-256 3EF4C2855A16C5A9... |
| DF42 | Produced in Step 31C by step31c_loso.py from DF41 and DF27 (model A) following the Study 2 protocol (DF40). Use: Predicted class and six class probabilities of models A, B and C for every held-out record, 3 variants. | File: 07_Experiments/2026-10-12_study2_loso/predictions.csv; SHA-256 8DFC514A73CB7D83... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 12. How this helps the next steps

Next step: Step 31D: measures with 95 % intervals, the paired contrasts B-A, C-B and C against the best conventional method, and the reject option (Tables 4.12-4.13, Figures 4.23-4.24).

•  Step 31D computes the measures, the paired contrasts and the reject option from these predictions only.

# 13. Open items and limitations

•  The inner-loop scores below are tuning scores on the training sources; they are not results. The held-out results follow in Step 31D.

•  The computer slept during the run; the time recorded for one fit (Li 2019, model B, primary) includes that pause and is not a computing time.

# 14. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| T2 | thermal fault 300 to 700 °C | Overheating in which the paper has carbonised. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| Random Forest | random forest | Many decision trees, each trained on a random sample; they vote for the answer. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Leakage | test cases hidden in the training data | If a model has already seen a test case, its score is falsely high. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Cross-validation | repeated train-and-test on parts of the training data | The data are split into parts; each part is used once for testing while the others train the model. |
| Fold | one part of the cross-validation split | Here the training data are cut into 5 folds (parts). |
| Stratified group k-fold | splitting method | Every part has the same mix of fault classes, and near-identical records stay together in one part. |
| Random seed | starting number for the random shuffle | Recording it means the same split can be made again exactly (seed 20261010). |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| venv | virtual environment | A private copy of Python and its libraries that belongs to this project only. |
| pytest | Python testing tool | Runs the automated checks that prove the data rules hold. |
| D1-D23 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Boundary distance | Distance to the nearest decision boundary | How far a sample is from the line where the diagnosis would change. A small distance means a small measurement error could change the diagnosis. |
| Feature set (F1-F4) | the inputs given to a model | F1 log gases, F2 gas percentages, F3 log-ratios and Duval percentages, F4 all of them (Analysis Plan 5.1). |
| Class weight | importance given to each record in training | w_c = N/(K n_c): rare classes get more weight so that every class counts equally (Analysis Plan Eq. 14). |
| Hyperparameter grid | list of settings tried for a model | For example C and gamma of the SVM; the best combination is chosen in the inner loop (Analysis Plan 5.2). |
| Macro-F1 | average F1 score over the classes | The primary performance measure; every class counts equally however rare it is. |
| Class probability | model's confidence in each class | For every record the model gives a probability for each of the seven classes; they add up to 1 and the largest is the prediction. |
| joblib | Python file format for saved models | Stores the fitted pipeline (preprocessing and model together) so it can be reloaded and give exactly the same predictions. |
| Boundary distance | how far a sample lies from a decision line | For the ratio methods in decades of the ratio, for Duval in percentage points to the nearest zone edge (Analysis Plan Eqs. 9-10). |
| Study 2 | exploratory improvement study | An extra study, planned after the main results, that tests ways to improve the model; reported separately from the main (confirmatory) results. |
| Leave-one-source-out | testing on a source never seen in training | Each data source is held out in turn; the model is trained on the other sources and tested on the held-out one, which measures how well it transfers to new data. |
| Hybrid model | machine learning plus expert rules | A model that receives the conventional methods' answers and boundary distances as extra inputs besides the gas features. |
| Reject option | the model may decline to answer | The model gives a diagnosis only when its highest class probability reaches a threshold; otherwise it reports no diagnosis (Chow, 1970). |