Step 31E Report

Interpret Study 2 against its decision rules

Environment: Claude Code (this chat)   |   Completed: 12 October 2026   |   Report version 1 (12 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: By its own rules, fixed before any Study 2 model was trained: (1) training on several sources is not shown to help, (2) adding the conventional methods' answers is not shown to help, and (3) letting the model decline uncertain cases is shown to make it at least as accurate as IEC 60599 at the same answer rate. The practical lesson is that the ML model is most useful as a 'confident or refer' tool. These results are exploratory and do not change the confirmatory verdict.

# 1. Purpose of this step

This step states what Study 2 shows and does not show, using only the decision rules written in its protocol.

# 2. Method used

## Approach

The three decision rules written in the Study 2 protocol before any model was trained were applied, by a program, exactly as written to the results of Step 31D, for the primary analysis and for the two sensitivity variants.

Rule 3 says the interval of the difference must be 'not below 0'. Because the results had already been seen when this wording was examined, the program applied both possible readings - lower limit at least 0 (strict) and estimate at least 0 (lenient) - and reports whether they agree.

## Why this method

•  Applying rules fixed in advance, by program, is what turns an exploratory study into an honest one: the conclusion cannot be shaped after seeing the numbers.

## Settings and rules

| Setting | Value |
| --- | --- |
| Rule 1 (pooling) | B - A macro-F1 > 0 with CI excluding 0 on at least 2 of 3 external sources |
| Rule 2 (hybrid) | C - B macro-F1 > 0 with CI excluding 0 on at least 2 of 4 held-out sources |
| Rule 3 (reject option) | model C at IEC 60599's coverage at least as accurate as IEC on at least 2 of 3 external sources; both readings applied |
| Status | EXPLORATORY |

## Tools and programs

•  06_Python_ML/src/study2/step31e_decisions.py

## Method references

[M32] C. K. Chow, "On optimum recognition error and reject tradeoff," IEEE Transactions on Information Theory, vol. 16, no. 1, pp. 41-46, 1970. doi: 10.1109/TIT.1970.1054406

# 3. What was done

1.  Wrote step31e_decisions.py and applied the rules to the Step 31D results for all three variants.

2.  For rule 3, applied both readings of 'not below 0' and checked that they agree.

# 4. Decisions of the rules

| Analysis | Pooling (B - A) | Hybrid (C - B) | Reject option (C vs IEC 60599) |
| --- | --- | --- | --- |
| Primary | Rule 1: NOT MET (0 of 3) | Rule 2: NOT MET (0 of 4) | Rule 3: MET strict (2 of 3), MET lenient (3 of 3) |
| Equal source weight | Rule 1: NOT MET (1 of 3) | Rule 2: NOT MET (1 of 4) | Rule 3: MET strict (3 of 3), MET lenient (3 of 3) |
| IEC TC 10 all 117 | Rule 1: MET (2 of 3) | Rule 2: NOT MET (1 of 4) | Rule 3: MET strict (3 of 3), MET lenient (3 of 3) |

## Per source (primary analysis)

•  Rule 1 - interval of B - A excludes 0: Dissanayake unseen no; IEC TC 10 no; Li 2019 no.

•  Rule 2 - interval of C - B excludes 0: Dissanayake training no; Dissanayake unseen no; IEC TC 10 no; Li 2019 no. The hybrid model is significantly WORSE when the Dissanayake training set is held out (DISTRAIN), where only 204 records remain for training.

•  Rule 3 - strict reading: Dissanayake unseen yes; IEC TC 10 no; Li 2019 yes; lenient reading: Dissanayake unseen yes; IEC TC 10 yes; Li 2019 yes.

# 5. What Study 2 shows and does not show

•  Shown (exploratory): a reject option is the most effective remedy. When the hybrid model answers only as many records as IEC 60599 does, keeping its most confident answers, it is more accurate than IEC 60599 on every source, clearly so on the Dissanayake and Li 2019 sources. For a utility this suggests a 'confident or refer' workflow: accept the model's diagnosis when it is confident, and send the rest to an engineer and to further tests.

•  Not shown: that training on several sources, or giving the model the conventional answers, improves performance on a new source by more than the uncertainty. The estimated gains on the external sources are mostly positive (for example, on IEC TC 10 the macro-F1 rises from 0.731 for the released model to 0.821 for the hybrid model), but the intervals include zero, and the sensitivity variants disagree.

•  Unchanged: the confirmatory verdict of Steps 22-31 (hypothesis not supported on the IEC TC 10 benchmark). Study 2 is reported separately and labelled exploratory.

# 6. Checks

| Check | Result |
| --- | --- |
| Rules applied by program, exactly as written in the protocol | PASS |
| Both readings of rule 3 lead to the same conclusion | PASS |
| Confirmatory results untouched | PASS |

# 7. Problems and fixes

•  The first run of the decision program stopped because the equal-source-weight variant had no model A predictions; Step 31D was corrected (model A reused for the same records) and re-run with identical primary results, then the rules were applied.

# 8. Decisions

•  No new decision (D28, D29).

# 9. Files produced

•  08_Statistical_Analysis/study2/study2_decisions.json; 06_Python_ML/src/study2/step31e_decisions.py; 03_Data/interim/step31e_report.md

# 10. What was achieved

•  Study 2 is decided by its pre-registered rules: pooling and the hybrid model are not shown to help; the reject option is shown to make the model competitive with IEC 60599.

•  The conclusion is the same under both readings of rule 3 and is reported beside, not instead of, the confirmatory results.

# 11. Record of this step

| Item | Record |
| --- | --- |
| Step | 31E - Interpret Study 2 against its decision rules |
| Environment | Claude Code (this chat) |
| Completed | 12 October 2026 |
| Status | Done - EXPLORATORY |
| Main inputs | 08_Statistical_Analysis/study2/contrasts.csv, reject_option.csv (Step 31D); Study 2 protocol |
| Main outputs | 08_Statistical_Analysis/study2/study2_decisions.json |
| Checks | rules applied by program; both readings of rule 3 agree |
| Decisions | none new (D28, D29) |

# 12. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DF43 | Produced in Step 31D by step31d_measures.py from DF42 and DF41 (protocol DF40, clarification D29). EXPLORATORY. Use: Macro-F1, accuracy, coverage with intervals; contrasts B-A, C-B, C-best; reject option. | File: 08_Statistical_Analysis/study2/measures.csv; SHA-256 E8E63171015FFF44... |
| DF40 | Written in Step 31A (decision D28) before any Study 2 model was trained; fingerprint recorded in 03_Data/study2/study2_protocol.sha256. Use: Fixes the questions, data rules, models, measures, statistics and decision rules of Study 2. | File: 00_Project_Admin/Study2_Protocol.docx; SHA-256 3EF4C2855A16C5A9... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 13. How this helps the next steps

Next step: Step 31F: search legitimate sources for a fresh set of inspection-confirmed DGA cases on which the reject-option result could be confirmed.

•  Step 31F searches for a fresh, legitimately licensed set of inspection-confirmed cases on which the reject-option result could be confirmed.

•  Chapter 4 reports Study 2 in its own exploratory section; Chapter 5 can recommend the reject option for practice.

# 14. Open items and limitations

•  Study 2 is exploratory: IEC TC 10 and Li 2019 had been seen before. The reject-option result needs confirmation on fresh data.

•  Most estimated gains of pooling and of the hybrid model are positive on the external sources, but too small for these sample sizes to confirm; 'not shown' does not mean 'no effect'.

•  In one sensitivity variant (all 117 IEC TC 10 records) rule 1 is met; in the primary analysis and the equal-weight variant it is not - the pooling result is therefore fragile.

# 15. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| D1-D23 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Feature set (F1-F4) | the inputs given to a model | F1 log gases, F2 gas percentages, F3 log-ratios and Duval percentages, F4 all of them (Analysis Plan 5.1). |
| Macro-F1 | average F1 score over the classes | The primary performance measure; every class counts equally however rare it is. |
| Coverage | share of records that get a diagnosis | 1 minus the share of no-diagnosis answers (Analysis Plan Eq. 6); the ML model always answers, so its coverage is 100 %. |
| Study 2 | exploratory improvement study | An extra study, planned after the main results, that tests ways to improve the model; reported separately from the main (confirmatory) results. |
| Confirmatory vs exploratory | tested as planned vs looked into afterwards | Confirmatory results test a hypothesis fixed in advance on untouched data; exploratory results come from analyses planned after seeing some results and need confirmation on new data. |
| Pre-registration | writing the plan before the analysis | The questions, data rules, methods and decision rules are fixed and fingerprinted before any result exists, so the analysis cannot be fitted to the results. |
| Hybrid model | machine learning plus expert rules | A model that receives the conventional methods' answers and boundary distances as extra inputs besides the gas features. |
| Reject option | the model may decline to answer | The model gives a diagnosis only when its highest class probability reaches a threshold; otherwise it reports no diagnosis (Chow, 1970). |