Step 31 Report

Test the boundary hypothesis

Environment: Claude Code (this chat)   |   Completed: 12 October 2026   |   Report version 1 (12 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: In the main analysis (205 test records, answers after the normality gate) disagreement between the ML model and a conventional method is not significantly more frequent near that method's decision boundaries: the odds ratios per standard deviation of distance are 0.80 (Rogers), 1.01 (IEC 60599) and 0.82 (Duval), all with intervals that include 1. Criterion 3 is therefore not met. When the gate is removed, Duval shows a clear boundary effect (OR 0.49, 95 % CI 0.34-0.69): the gate's Normal answers hide it. With all three criteria decided, the research hypothesis is NOT SUPPORTED on the main benchmark, exactly as the written rule requires.

# 1. Purpose of this step

This step answers RQ2 - where do the ML model and the conventional methods disagree, and is the disagreement concentrated near the conventional decision boundaries? - and decides criterion 3, completing the judgement of the research hypothesis.

# 2. Method used

## Approach

For each conventional method, every primary test record was marked as a disagreement (the ML answer differs from the method's answer) or not. A logistic regression then modelled the probability of disagreement against the record's distance to the nearest decision boundary of that method, standardised to a z-score (Analysis Plan Eq. 33). The odds ratio per standard deviation of distance, with its 95 % confidence interval, is the effect size (Eq. 34).

The main analysis pools the 205 records of the three primary test sets and uses the answers after the normality gate. Sensitivity analyses repeat it with the raw answers (gate removed), for each test set separately, and with test-set indicators. The details were fixed as decision D27 before any model was fitted.

Criterion 3 of the research hypothesis is met for a method when the coefficient is negative and its 95 % interval excludes zero; the hypothesis needs it for each method.

## Why this method

•  If the ML model mostly disagrees with a conventional method close to that method's decision lines, the disagreement reflects borderline cases where a fixed rule is uncertain - the mechanism proposed in RQ2.

•  Logistic regression is the standard model for a yes/no outcome; the odds ratio per standard deviation makes the three methods comparable although their distances are in different units.

•  Firth's penalised regression (Firth, 1993) was kept ready for complete separation; it was not needed.

## Settings and rules

| Setting | Value |
| --- | --- |
| Records | 205 primary test records (internal 61, IEC TC 10 58, Li 2019 86); excluded for an undefined or infinite distance: Rogers 1, IEC 1, Duval 0 |
| Disagreement | ML answer different from the method's answer; no diagnosis = disagreement; IEC D1/D2 agrees with ML D1 or D2; merged classes on IEC TC 10 |
| Distance | Steps 14-17: IEC and Rogers in decades of the ratio (Eq. 9), Duval in percentage points (Eq. 10); z-score over the records used |
| Model | maximum-likelihood logistic regression; Firth if separation (not needed); Wald 95 % CI |
| Criterion 3 | beta1 < 0 and 95 % CI of the odds ratio below 1, for each method |

## Equations

lnπi1-πi=β0+β1di#1

where:

πi  –  probability that record i is a disagreement case

di  –  standardised boundary distance of record i (z-score)

β1  –  change in the log-odds of disagreement per standard deviation of distance

OR=eβ1  95 % CI=eβ1±1.96SEβ1#2

where:

"  –  O

o  –  d

## Tools and programs

•  06_Python_ML/src/stats/step31_boundary.py (data, logistic and Firth regression, Table 4.8, Figure 4.12, criterion 3)

•  tests/test_boundary.py (3 tests: equal to statsmodels; Firth finite under separation; disagreement rule)

## Method references

[M31] D. Firth, "Bias reduction of maximum likelihood estimates," Biometrika, vol. 80, no. 1, pp. 27-38, 1993. doi: 10.1093/biomet/80.1.27

[M21] E. B. Wilson, "Probable inference, the law of succession, and statistical inference," Journal of the American Statistical Association, vol. 22, no. 158, pp. 209-212, 1927. doi: 10.1080/01621459.1927.10502953

# 3. What was done, step by step

1.  Fixed the details as decision D27 before fitting any model (only the number of records without a distance had been looked at: one record for each ratio method).

2.  Wrote step31_boundary.py with a logistic and a Firth regression, and tests comparing it with statsmodels.

3.  Ran it; corrected the per-set count of excluded records (the first run showed each method's total in every set) and ran it again - the fitted models were unchanged.

# 4. What we found

## Table 4.8 - disagreement against boundary distance (main analysis)

| Method | Records | Excluded | Disagree | beta1 | OR per SD [95 % CI] | p | Criterion 3 met? |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Rogers Ratio | 204 | 1 | 133 | -0.222 | 0.80 [0.60, 1.07] | 0.137 | no |
| IEC 60599 ratio | 204 | 1 | 97 | 0.010 | 1.01 [0.77, 1.33] | 0.945 | no |
| Duval Triangle 1 | 205 | 0 | 103 | -0.197 | 0.82 [0.62, 1.08] | 0.164 | no |

Figure 4.12  Probability of disagreement against standardised boundary distance (205 primary test records)

Line and band: fitted logistic curve with 95 % band; points: observed disagreement rate in ten equal-sized distance groups with Wilson 95 % bars; ticks: individual records (top = disagree, bottom = agree). A curve that falls from left to right supports the boundary hypothesis.

## Sensitivity analyses (odds ratio per SD [95 % CI])

| Method | Gate | Analysis | Records | OR per SD [95 % CI] | p | Crit. 3 |
| --- | --- | --- | --- | --- | --- | --- |
| Rogers Ratio | with gate | pooled (main) | 204 | 0.80 [0.60, 1.07] | 0.137 | no |
| Rogers Ratio | with gate | pooled + test-set indicators | 204 | 0.78 [0.58, 1.05] | 0.107 | no |
| Rogers Ratio | with gate | Internal test | 61 | 1.29 [0.63, 2.63] | 0.485 | no |
| Rogers Ratio | with gate | IEC TC 10 (power transformers) | 58 | 0.36 [0.19, 0.71] | 0.003 | yes |
| Rogers Ratio | with gate | Li 2019 | 85 | 0.65 [0.41, 1.03] | 0.067 | no |
| Rogers Ratio | no gate | pooled (main) | 204 | 0.85 [0.64, 1.13] | 0.268 | no |
| Rogers Ratio | no gate | pooled + test-set indicators | 204 | 0.84 [0.63, 1.12] | 0.232 | no |
| Rogers Ratio | no gate | Internal test | 61 | 1.24 [0.66, 2.33] | 0.497 | no |
| Rogers Ratio | no gate | IEC TC 10 (power transformers) | 58 | 0.28 [0.13, 0.59] | < 0.001 | yes |
| Rogers Ratio | no gate | Li 2019 | 85 | 0.85 [0.54, 1.31] | 0.454 | no |
| IEC 60599 ratio | with gate | pooled (main) | 204 | 1.01 [0.77, 1.33] | 0.945 | no |
| IEC 60599 ratio | with gate | pooled + test-set indicators | 204 | 0.94 [0.71, 1.25] | 0.683 | no |
| IEC 60599 ratio | with gate | Internal test | 61 | 1.33 [0.70, 2.54] | 0.384 | no |
| IEC 60599 ratio | with gate | IEC TC 10 (power transformers) | 58 | 0.69 [0.36, 1.34] | 0.276 | no |
| IEC 60599 ratio | with gate | Li 2019 | 85 | 0.73 [0.46, 1.16] | 0.188 | no |
| IEC 60599 ratio | no gate | pooled (main) | 204 | 0.97 [0.74, 1.29] | 0.858 | no |
| IEC 60599 ratio | no gate | pooled + test-set indicators | 204 | 0.90 [0.67, 1.20] | 0.475 | no |
| IEC 60599 ratio | no gate | Internal test | 61 | 1.14 [0.66, 1.98] | 0.630 | no |
| IEC 60599 ratio | no gate | IEC TC 10 (power transformers) | 58 | 0.68 [0.33, 1.37] | 0.280 | no |
| IEC 60599 ratio | no gate | Li 2019 | 85 | 0.72 [0.44, 1.17] | 0.190 | no |
| Duval Triangle 1 | with gate | pooled (main) | 205 | 0.82 [0.62, 1.08] | 0.164 | no |
| Duval Triangle 1 | with gate | pooled + test-set indicators | 205 | 0.82 [0.62, 1.09] | 0.180 | no |
| Duval Triangle 1 | with gate | Internal test | 61 | 1.04 [0.63, 1.74] | 0.867 | no |
| Duval Triangle 1 | with gate | IEC TC 10 (power transformers) | 58 | 0.67 [0.37, 1.23] | 0.198 | no |
| Duval Triangle 1 | with gate | Li 2019 | 86 | 0.77 [0.50, 1.19] | 0.243 | no |
| Duval Triangle 1 | no gate | pooled (main) | 205 | 0.49 [0.34, 0.69] | < 0.001 | yes |
| Duval Triangle 1 | no gate | pooled + test-set indicators | 205 | 0.48 [0.34, 0.69] | < 0.001 | yes |
| Duval Triangle 1 | no gate | Internal test | 61 | 0.66 [0.39, 1.14] | 0.135 | no |
| Duval Triangle 1 | no gate | IEC TC 10 (power transformers) | 58 | 0.57 [0.30, 1.11] | 0.100 | no |
| Duval Triangle 1 | no gate | Li 2019 | 86 | 0.29 [0.14, 0.59] | < 0.001 | yes |

## What this means

•  With the approved gate, none of the three methods shows a significant boundary effect when all test records are pooled. Two methods have odds ratios below 1 (fewer disagreements far from the boundary), in the direction the hypothesis expects, but the evidence is not strong enough.

•  Without the gate, Duval shows a strong boundary effect: each standard deviation further from a zone edge roughly halves the odds of disagreement (OR 0.49). The gate turns many low-gas faults into Normal answers, which disagree with the ML model wherever they lie in the triangle and so mask the boundary pattern.

•  Rogers shows a significant boundary effect on the IEC TC 10 set alone, but IEC 60599 and Duval do not, so criterion 3 is not met on the main benchmark either.

## Final judgement of the research hypothesis (Analysis Plan Section 2.1)

| Test set | Criterion 1 (more accurate, significant) | Criterion 2 (advantage from ND cases) | Criterion 3 (boundary effect, per set) |
| --- | --- | --- | --- |
| Internal test | met | not met (Duval) | Rogers no, IEC no, Duval no -> not met |
| IEC TC 10 (power transformers) | not met | not met (Duval) | Rogers yes, IEC no, Duval no -> not met |
| Li 2019 | met | not met (Duval) | Rogers no, IEC no, Duval no -> not met |

•  Verdict on the main benchmark (IEC TC 10 power transformers, decision D26): NOT SUPPORTED. The ML model is not significantly more accurate than IEC 60599 or Duval there, and the disagreements are not concentrated near the boundaries.

•  On the internal and Li 2019 test sets the hypothesis is partly supported: criterion 1 is met (with the approved gate) and criterion 2 is met against Rogers and IEC 60599, but criteria 2 (against Duval) and 3 are not.

•  This is reported as found. It is a meaningful result: a carefully validated ML model does not clearly outperform a well-established expert method on inspection-confirmed cases, while it does on data like its training data and keeps its accuracy with fewer gases (Step 27).

# 5. Checks

| Check | Result |
| --- | --- |
| Data version 1.0 and merged file unchanged (SHA-256) | PASS |
| Logistic regression equals statsmodels; Firth finite under separation (automated tests) | PASS |
| No separation occurred (all fits by maximum likelihood) | PASS |
| Text statements checked against the result files by the report builder | PASS |
| Full automated test suite | PASS - 120 of 120 tests pass |

# 6. Problems and fixes

•  The first run reported each method's total number of excluded records in every per-set row; the count is now computed per set. Fitted models and conclusions did not change.

# 7. Decisions

•  D27 (procedural, within the approved plan): records, disagreement rule, gate sensitivity, distances, Firth fallback, how criterion 3 is read.

# 8. Files produced

•  08_Statistical_Analysis/boundary_regression.csv, boundary_data.csv; hypothesis_criteria.json (criterion 3 and verdict added)

•  11_Results/tables/T4_8_boundary.csv; 11_Results/figures/F4_12_disagreement_vs_distance (PNG, PDF, CSV)

•  06_Python_ML/src/stats/step31_boundary.py; 06_Python_ML/tests/test_boundary.py; 03_Data/interim/step31_report.md

# 9. What was achieved

•  The boundary hypothesis (RQ2) was tested for all three conventional methods, with sensitivity analyses.

•  All three criteria of the research hypothesis are now decided, and the verdict follows exactly the written rule.

•  Table 4.8 and Figure 4.12 are produced with their data files.

# 10. Record of this step

| Item | Record |
| --- | --- |
| Step | 31 - Test the boundary hypothesis |
| Environment | Claude Code (this chat) |
| Completed | 12 October 2026 |
| Status | Done |
| Main inputs | 08_Statistical_Analysis/merged_predictions.csv (Step 28); hypothesis_criteria.json (Step 30) |
| Main outputs | 08_Statistical_Analysis/boundary_regression.csv, boundary_data.csv; hypothesis_criteria.json (completed); Table T4_8; Figure F4_12 |
| Checks | regression equals statsmodels; exclusion counts per set corrected and re-run; 120 of 120 tests pass |
| Decisions | D27 (boundary analysis details; procedural) |

# 11. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DF34 | Produced in Step 28 by step28_merge_predictions.py from DF2, DF9 (conventional predictions) and DF25 (ML predictions). Use: True class, flags, ML prediction and probabilities, conventional answers (raw, upper gate, lower gate, merged classes), boundary distances. | File: 08_Statistical_Analysis/merged_predictions.csv; SHA-256 EDB799A2CDA41A69... |
| DF37 | Produced in Step 30 by step30_tests.py from DF21 (fold results) and DF34 (merged predictions); decision D26. Use: McNemar (Holm), Cochran's Q, Friedman/Nemenyi, kappa, hypothesis criteria. | File: 08_Statistical_Analysis/cochran_mcnemar.csv; SHA-256 CCC3414122D688BB... |
| DF39 | Produced in Step 31 by step31_boundary.py from DF34 (decision D27). Use: Logistic regression of ML-method disagreement on boundary distance; criterion 3. | File: 08_Statistical_Analysis/boundary_regression.csv; SHA-256 0CB49CA5E7B168D4... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |

# 12. How this helps the next steps

Next step: Step 32: one script rebuilds every Chapter 4 table and figure from the saved files (including Figures 4.6, 4.9, 4.10 and 4.13) in the style of Analysis Plan Section 12.2; deleting 11_Results and running it again must give identical files.

•  Step 32 rebuilds every Chapter 4 table and figure, including Figure 4.13 (disagreements in the Duval Triangle), from the saved files.

•  Chapter 5 (discussion) can explain why the hypothesis was not supported and what the gate and the boundary results mean for practice.

# 13. Open items and limitations

•  The distances of the ratio methods are strongly right-skewed (a few records lie far from any limit), so a few records influence the fitted slope; the plan's z-score scale was kept as written.

•  Disagreements caused by the normality gate are not related to any ratio or zone boundary; this is why the raw-answer sensitivity analysis is reported beside the main one.

•  With 58 records the IEC TC 10 analysis has little power; a non-significant slope is not evidence that no boundary effect exists.

# 14. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| Normal (class 0) | no fault | A transformer without a fault: its gases stay at the levels normally found in service. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| D2 | discharges of high energy | Arcing with power follow-through: extensive carbonisation, metal fusion, sometimes tripping of the equipment. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| Ratio method | diagnosis from gas ratios | Divides one gas by another (for example C2H2/C2H4) and compares the result with fixed limits to name the fault. |
| Duval Triangle 1 | graphical DGA method by M. Duval | The shares of CH4, C2H4 and C2H2 are plotted as one point in a triangle divided into fault zones. |
| Rogers ratios | older gas-ratio method by R.R. Rogers | A ratio table that names faults from three gas ratios; kept in IEEE C57.104. |
| Normality gate | rule that lets conventional methods answer 'Normal' | If all gases are below their typical values, the conventional methods give Normal instead of a fault (decision D3). |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Logistic regression | multinomial logistic regression | A simple, explainable model that turns weighted gas values into class probabilities. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Internal test set | Dissanayake unseen test file | 70 records (61 independent of the benchmark) kept away from training. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Fold | one part of the cross-validation split | Here the training data are cut into 5 folds (parts). |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| PNG, PDF, dpi | image file, printable document file, dots per inch | Figures are saved as PNG at 300 dpi (sharp for printing) and as PDF. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| venv | virtual environment | A private copy of Python and its libraries that belongs to this project only. |
| pytest | Python testing tool | Runs the automated checks that prove the data rules hold. |
| D1-D23 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |
| ND (no diagnosis) | No diagnosis | The answer of a method when no rule applies or a ratio it needs cannot be calculated. It is a result and is never deleted. |
| Dual answer (D1/D2) | Two classes returned together | Sometimes the IEC table fits two fault types at once. The method then answers with both (D1/D2); it counts as correct if the true class is either one. |
| Boundary distance | Distance to the nearest decision boundary | How far a sample is from the line where the diagnosis would change. A small distance means a small measurement error could change the diagnosis. |
| Decade (log10 unit) | A factor of 10 | A distance of 1 decade on the ratio scale means the ratio is 10 times larger or smaller, e.g. from 0.1 to 1. |
| Feature set (F1-F4) | the inputs given to a model | F1 log gases, F2 gas percentages, F3 log-ratios and Duval percentages, F4 all of them (Analysis Plan 5.1). |
| Standardisation (z-score) | rescaling a feature | Subtract the training-fold mean and divide by the training-fold standard deviation (Analysis Plan Eq. 13). |
| SD | standard deviation | How much the 50 fold values spread around their mean; a small SD means the result is stable from fold to fold. |
| Kappa | Cohen's kappa | Agreement between predicted and true classes after removing the agreement expected by chance: 0 = chance, 1 = perfect. |
| Friedman and Nemenyi tests | rank-based comparison of several models | Friedman tests whether models' average ranks over the folds differ; Nemenyi then shows which pairs differ (Step 30). |
| Class probability | model's confidence in each class | For every record the model gives a probability for each of the seven classes; they add up to 1 and the largest is the prediction. |
| Wilson interval | confidence interval for a proportion | A 95 % interval for an accuracy or a coverage that works well for small samples (Analysis Plan Eq. 21). |
| McNemar test | paired test of two methods on the same records | Uses only the records where one method is right and the other wrong (b and c); tests whether b and c differ more than chance (Analysis Plan Eqs. 30-31). |
| Cochran's Q | test of several methods on the same records | Tests whether all methods have the same share of correct answers before the pairwise tests (Analysis Plan Eq. 29). |
| Holm correction | adjustment for several tests | Keeps the chance of any false positive among the three comparisons per test set at 5 % (Analysis Plan Eq. 32). |
| Odds ratio b/c | effect size of the McNemar test | How many times more often the ML model was right where the other method was wrong than the reverse; 1 = no difference. |
| Logistic regression (of disagreement) | model for a yes/no outcome | Estimates how the chance that ML and a conventional method disagree changes with the distance to the nearest decision boundary (Analysis Plan Eq. 33). |
| Boundary distance | how far a sample lies from a decision line | For the ratio methods in decades of the ratio, for Duval in percentage points to the nearest zone edge (Analysis Plan Eqs. 9-10). |