Step 34 Report

Run the model checks

Environment: Claude Code (this chat), MATLAB and Simulink through the MCP connection   |   Completed: 13 October 2026   |   Report version 1 (13 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The transformer operating model was checked in two ways: with the Model Advisor of Simulink Check (132 checks) and with the checklist of Part D1 of the MATLAB Build Guide. The first Model Advisor run on the Step 33 model gave 115 passed, 16 warnings, 1 incomplete, 0 failed; five groups of warnings were fixed in the building program and the final run gives 120 passed, 11 warnings, 1 incomplete, 0 failed. Nothing failed. The 12 results that are not 'passed' are style rules for control code, code-generation options or internals of Simscape library blocks; each has a written reason, and their acceptance is proposed to the researcher (decision D32). The stricter scan of every dialog field of all 84 blocks found one real typed parameter number that Step 33 had missed (the transformer's zero-sequence reactance, the block default 0.5); it is now the variable X0_pu. After all changes the nine checks of Step 33 still pass and the 24-hour run is unchanged (load factor 0.9839, top oil 78.638 degC, hot spot 100.276 degC). One checklist item, a second person checking the build, needs a person and stays open.

# 1. Purpose of this step

A model that is going to be used for a thesis must be checked before it is verified against theory. This step asks the computer to inspect the model without running it: are there unconnected ports, settings that hide errors, outdated blocks, numbers typed into blocks, missing notes? Every finding must either be fixed or be accepted with a written reason. Step 35 then compares the model with the IEC 60076-7 equations.

# 2. Method used

## Approach

Static model checking in two parts. Part 1 is the Model Advisor of Simulink Check: a MathWorks tool that opens the model without running a simulation and applies a list of rules (settings, unconnected ports and lines, deprecated blocks, units, style rules). A MATLAB program (step34_run_model_advisor.m) starts it with a fixed list of 132 checks and saves the report. Part 2 is the checklist of Part D1 of the MATLAB Build Guide, written as a MATLAB function (step34_checklist_D1.m) so that it can be repeated at any time.

Every result that is not 'passed' was read and then handled in one of two ways, as the roadmap requires: fixed, or accepted with a written reason. A fix is never made by hand in the model file; it is made in the building program (build_Transformer_Operating_Model.m), the model is rebuilt, and all earlier checks (the nine checks of Step 33) are run again. An acceptance is written into a table by a program that stops if a non-passed check has no reason.

The checklist item 'no number typed into a block' was tested more strictly than in Step 33: the program reads every dialog field of every one of the 84 blocks (not only the settings that the builder made), picks out the values that contain a digit and sorts them by rule into harmless categories or into 'parameter number'. The item passes only if the category 'parameter number' is empty.

## Why this method

•  Checking a model before it is used is standard practice in model-based design; the Model Advisor is the tool MathWorks provides for it, and 'fix it or justify it' is the same logic as the justification feature of the Model Advisor itself.

•  Fixing in the building program keeps the model reproducible: anyone who runs the program gets the corrected model, and nothing exists only in a hand-edited file.

•  Re-running all earlier checks after every change shows that a fix did not change the physics (here the logged signals stay identical to the reference run, difference 0.00e+00).

•  A strict scan of all dialog fields is the only way to find numbers that a person would not see at first glance (hidden or default fields); it found one real case that Step 33 had missed.

## Settings and rules

| Setting | Value |
| --- | --- |
| Model Advisor check set | 132 checks: groups design, simscape, simulink, sl, maab (modelling and Simscape checks). Left out: code generation, AUTOSAR, DO-178, MISRA, PLC, HISM, JMAAB - no code is generated from this model (decision D32). |
| Result classes | Passed, Warning, Failed, Incomplete (Model Advisor terms) |
| Report | HTML, 05_Simulink_Model/checks/model_advisor_report.html |
| Tolerance for the 24 h run | 0.1 K against the Build Guide Section B12 values (K = 0.9839; top oil 78.638 degC; hot spot 100.276 degC); approved tolerance of the Analysis Plan, Section 9 |
| Categories of dialog values | interface code (port number, inherited sample time -1, latency, unit selector, normalisation value, logging option); hidden field (the block mask hides it); library tuning (tolerances and filter settings of Solver Configuration and converter blocks); option selector (0 = None); parameter number (anything else = fail) |
| Diagnostics set to error | Inf/NaN output, unconnected input, output and line, duplicate data store names, bus signal treated as vector |
| Software | MATLAB 25.2.0.2998904 (R2025b), Simulink, Simscape, Simscape Electrical, Simulink Check |

## Tools and programs

•  05_Simulink_Model/checks/step34_run_model_advisor.m (runs the checks, writes report and result table)

•  05_Simulink_Model/checks/step34_write_accepted.m (reasons for the non-passed checks), step34_checklist_D1.m (checklist)

•  05_Simulink_Model/build_Transformer_Operating_Model.m, verify_step33.m, params_transformer.m (changed in this step)

•  00_Project_Admin/report_builder/update_register_step34.ps1 (register, glossary)

## Method references

[SW5] The MathWorks, Inc. Simulink Check / Model Advisor, MATLAB R2025b (25.2.0.2998904). Function ModelAdvisor.run; check groups mathworks.design, mathworks.simscape, mathworks.simulink, mathworks.sl, mathworks.maab (132 checks). https://www.mathworks.com/help/slcheck/ref/modeladvisor.run.html

[SW2] MATLAB R2025b, version 25.2.0.2998904, The MathWorks, Inc., Natick, MA, USA. https://www.mathworks.com/products/matlab.html

[ST6] IEC 60076-7:2018, Power transformers - Part 7: Loading guide for mineral-oil-immersed power transformers (Edition 2.0). The full text was NOT obtained; details TO VERIFY.

# 3. What was used

•  Transformer_Operating_Model.slx as built in Step 33, params_transformer.m and build_Transformer_Operating_Model.m.

•  MATLAB Build Guide, Part D1 (checklist before the work is accepted) and Section B12 (expected results of the 24-hour run).

•  The Model Advisor of Simulink Check, MATLAB R2025b.

•  verify_step33.m (the nine checks of Step 33), used again after every change.

# 4. What was done, step by step

1.  Listed the Model Advisor checks and chose the set (decision D32): all checks of the groups design, simscape, simulink, sl and maab; the code-generation groups were left out.

2.  Ran the 132 checks on the Step 33 model (first run: 115 passed, 16 warnings, 1 incomplete, 0 failed). Read every warning and decided: fix or accept.

3.  Fixed five groups of warnings in the building program, rebuilt the model and ran the nine Step 33 checks again.

4.  Wrote the checklist function for Part D1, ran it, and corrected two faults of my own checker (see Problems and fixes). The stricter scan of all dialog fields found the zero-sequence reactance typed as 0.5; it became the variable X0_pu. The model was rebuilt and all checks were run again.

5.  Ran the Model Advisor a final time on the final model, wrote the table of accepted warnings with a reason for each, and the code fingerprints.

6.  Wrote this report and updated the register, the glossary, the READMEs, the decision log (D32), CHANGELOG.md and SESSION_SUMMARY.md.

# 5. What we found

## Model Advisor result

| Run | Passed | Warning | Failed | Incomplete |
| --- | --- | --- | --- | --- |
| First run (Step 33 model) | 115 | 16 | 0 | 1 |
| Final run (final model) | 120 | 11 | 0 | 1 |

Both runs applied the same 132 checks. 'Warning' means that the model works but a recommended setting or style rule is not met; 'Incomplete' means that the check itself stopped before it could give a result. The report file is 05_Simulink_Model/checks/model_advisor_report.html; the result of every check is in model_advisor_results.csv.

## What the first run reported and what was done

| Check (identifier) | What it said | What was done |
| --- | --- | --- |
| mathworks.design.UpdateRequireCompile | The 'sqrt' function of the Math Function block is deprecated. | Fixed: the Sqrt block (same operator) replaces it; the logged results are identical. |
| mathworks.design.DataStoreMemoryBlkIssue | 'Duplicate data store names' is not set to error. | Fixed: set to error (the model has no data stores). |
| mathworks.maab.jc_0021 | Five diagnostics are set to 'none': Inf or NaN output, unconnected input, output and line, duplicate data store names. | Fixed: all set to error, so a bad value or an open connection stops the run. |
| mathworks.design.BusTreatedAsVector | The model is not set to detect a bus signal treated as a vector. | Fixed: set to error (the model has no buses). |
| mathworks.maab.jc_0061 | The name of the Exp block is hidden. | Fixed: name shown (it needed 'Hide automatic name' switched off, not only 'Show name' on). |
| 11 other warnings and 1 incomplete check | Style rules for control code, code-generation options, library internals, and one check that stopped with a tool fault. | Accepted with a reason each: see the next table. |

## Results accepted with a written reason

| Check | Status | Blocks flagged | Reason |
| --- | --- | --- | --- |
| mathworks.design.OptimizationSettings | Warning | 0 | Recommends code-generation optimisations (bitsets for state and Boolean data). The model is used for simulation only; no code is generated from it. |
| mathworks.maab.na_0005 | Warning | 15 | The names of the Inport/Outport blocks of subsystems (K_pu, Q_oil, theta_oil_C ...) are hidden on the diagram (Format > Auto Name > Hide Automatic Block Names). Display only; the signals are described in the annotations. Not changed, so that the Step 33 figures stay valid. |
| mathworks.maab.na_0027 | Warning | 35 | MAAB list of allowed blocks for control models. The Simscape and Simscape Electrical blocks are required by the project (physical network) and are not on that list. |
| mathworks.maab.db_0141 | Warning | 4 | Layout rule (signal flow from left to right), flagged for SS1, SS3, SS4, SS6 and the top level. It concerns the arrangement of blocks on the diagram only; no effect on results. |
| mathworks.maab.hd_0001 | Warning | 4 | Rule against sink blocks in discrete hardware-design controllers. The four To Workspace blocks of SS7 log the results of a continuous plant model; they are the model's output. |
| mathworks.maab.na_0008 | Warning | 19 | Style rule asking for a label on some signal lines (those leaving or entering subsystem ports and converter blocks). The blocks are named and annotated; no effect on results. |
| mathworks.maab.db_0110 | Warning | 6 | Tunable parameters used inside expressions (for example log(2)/dT_double_age). This is intended: all values come from params_transformer.m, which is the project rule. |
| mathworks.maab.db_0140 | Warning | 17 | Style rule asking to display block parameters under the blocks. The values are in the block dialogs and are listed in results/step33_block_settings.csv; display only. |
| mathworks.maab.na_0004 | Warning | 35 | Non-standard colours and information overlays. The colour code (blue electrical, green arithmetic, orange thermal) is intentional and explained in the annotations. |
| mathworks.maab.na_0030 | Incomplete | 0 | The Model Advisor check itself stopped with the message 'Dot indexing is not supported for variables of this type' (tool fault, status Incomplete). Replaced by a direct test: the model contains no Bus Creator and no Bus Selector block (test 'no bus signals' in step34_checklist_D1.m), so there is no bus signal name to check. |
| mathworks.maab.na_0011 | Warning | 16 | All flagged From/Goto blocks are inside blocks of the Simscape library (the EVAL_KEY parts of the converter and Solver Configuration blocks); they were not placed by the model author and cannot be changed. |
| mathworks.design.StowawayDoubles | Warning | 26 | Recommendation for strict single-precision design. The model uses double precision on purpose (temperatures are compared to 0.1 K over 24 h). |

'Blocks flagged' is the number of model paths named in the check's text (0 when the check flags a setting or the whole model). The table is written by step34_write_accepted.m, which stops if a non-passed check has no reason. The acceptance is proposed in decision D32 and awaits the researcher's confirmation.

## Build Guide Part D1

| Item | What was tested | Result |
| --- | --- | --- |
| D1.1 | params_transformer.m runs | PASS |
| D1.1 | every variable has a unit [..] in its comment | PASS |
| D1.1 | every variable has a source or basis in its comment or section heading | PASS |
| D1.2 | no block dialog holds a typed parameter number (all dialog fields of all blocks read) | PASS |
| D1.3 | top level and every subsystem has an annotation | PASS |
| extra | no bus signals (substitute for the incomplete Model Advisor check na_0030) | PASS |
| D1.4 | Update Diagram gives no error | PASS |
| D1.4 | Update Diagram gives no warning | PASS |
| D1.4 | 24 h run: load factor K equals B12 (0.9839, 4 decimals) | PASS |
| D1.4 | 24 h run: top-oil temperature equals B12 within 0.1 K | PASS |
| D1.4 | 24 h run: hot-spot temperature equals B12 within 0.1 K | PASS |
| D1.5 | run_transformer_simulation returns non-empty results | PASS |
| D1.6 | the app runs (dashboard) | Not applicable yet |
| D1.7 | a second team member checked the build against the reference script | OPEN |

Details: the 24-hour run gives K = 0.9839, top-oil temperature 78.638 degC (difference to Section B12: 0.0005 K) and hot-spot temperature 100.276 degC (difference 0.0002 K); the tolerance is 0.1 K. Item D1.6 (the app) cannot be tested because the dashboard is built in a later stage. Item D1.7 (a second team member checks the build) needs a person. The row 'extra' is a direct test for bus blocks that replaces the incomplete Model Advisor check on bus signal names.

## Every dialog field of every block

Step 33 checked the numbers that the building program had set (109 settings). This step read every dialog field of all 84 blocks, including fields that the program never touched. 245 values contain a digit. They were sorted by rule, and every value with its category is in step34_block_numbers.csv.

| Category | Values | Meaning |
| --- | --- | --- |
| Interface code |  | 174 |
| Hidden field |  | 29 |
| Library tuning |  | 40 |
| Option selector |  | 2 |
| Parameter number | 0 | A typed number that should be a variable. None remains. |

The scan found one visible and enabled physical value: the zero-sequence reactance of the transformer, pu_X0 = 0.5, which was the library default. It is now the variable X0_pu in params_transformer.m. The value is unchanged, the source is the block default and not the pandapower data (TO VERIFY), and it has no effect on a balanced load.

## Parameter file

params_transformer.m defines 47 variables. The check requires a unit in square brackets and a source or basis for every one: a source code (E1, T1, T2, A1 to A4), an explicit basis in the comment, or a basis stated in the section heading (Sections 1 and 3 name E1 and T1; Sections 2 and 4 name the Build Guide, Section A3, for derived values; Section 5 states that its values are run settings chosen for the verification run). The check found real gaps: the load profile had no unit and the two ageing constants had no source tag. They now carry the unit and the source codes of the Build Guide (A4, reference T2: the IntechOpen chapter, marked TO VERIFY against IEC 60076-7). Only comments were changed, except for the new variable X0_pu.

## Changes made to the model and its programs

| Change | Why | Where |
| --- | --- | --- |
| Sqrt block instead of Math Function 'sqrt' | Deprecated block (Model Advisor). | build_Transformer_Operating_Model.m, SS3_LV_Measurement/Square_Root |
| Six diagnostics set to error | Silent Inf/NaN values and open connections would go unnoticed. | build_Transformer_Operating_Model.m, model settings |
| Name of the Exp block shown | Model Advisor style check. | SS7_Outputs_and_Ageing/Exp |
| Variable X0_pu (0.5 pu) for the zero-sequence reactance | No number typed into a block (Build Guide D1.2). | params_transformer.m; SS2 transformer block; annotation of SS2 |
| Units and source tags in the parameter file | Build Guide D1.1. | params_transformer.m (comments) |
| Expected differences extended to 7 | verify_step33.m compares the model with the reference build; the Sqrt block (type, algorithm) and X0_pu are new, documented differences. The logged results are identical to the reference. | verify_step33.m, check 3 |

# 6. Checks

| Check (verify_step33.m, run again after the final rebuild) | Result |
| --- | --- |
| opens, updates and simulates from a clean path | PASS |
| no warning during update/simulation | PASS |
| model and all 7 subsystems carry an annotation; every subsystem has a Description | PASS |
| no number typed into a block (all settings are variables or equation constants) | PASS |
| no block produces or names a gas concentration | PASS |
| exactly one Solver Configuration per physical network (electrical, thermal) | PASS |
| structure equals the reference model (blocks, parameters, connections) | PASS |
| 24 h run equals the analytic steady state of the IEC 60076-7 equations (<= 0.1 K) | PASS |
| results equal the reference model (logged signals, same run) | PASS |

Detail of the structure check: 84 blocks compared; 7 expected differences (273.15 -> T_zero_C_in_K; Sqrt block and X0_pu, Step 34); 0 unexpected. The largest difference between this model and the reference run is 0.00e+00, so the fixes did not change the physics.

# 7. Problems and fixes

•  My first version of the parameter-file check reported that almost every variable lacked a source. The cause was my own search pattern: in MATLAB regular expressions the code \b means the backspace character, not a word boundary. The pattern now uses look-around expressions. After the repair, the lines that rely on the section heading for their basis (derived values, run settings) were still listed; the rule was widened so that a basis stated in the section heading counts, and Section 5 now states its basis.

•  The first scan of the dialog fields listed 246 values, nearly all of them harmless. Instead of ignoring the list, every value was given a category by a written rule; the one real finding (pu_X0) was fixed. The classification rules are in the comments of step34_checklist_D1.m.

•  After the first rebuild verify_step33.m gave 8 of 9: the Sqrt block has another block type and the algorithm label 'Exact' instead of 'Newton-Raphson'. As the logged results are identical, both were added as expected differences with the reason stated, and X0_pu was added the same way later. The check still finds every other difference.

•  Two fixes did not take effect at first: the bus setting needed the value 'ErrorOnBusTreatedAsVector' (not 'ErrorLevel1'), and the Exp block name needed 'Hide automatic name' switched off. The Model Advisor, run again, showed this; both were corrected in the building program.

•  The Model Advisor check on bus signal names (mathworks.maab.na_0030) stops with the message 'Dot indexing is not supported for variables of this type' inside the tool. It was replaced by a direct test (the model has no Bus Creator or Bus Selector block).

•  The raw file of the first Model Advisor run was overwritten by the later runs. Its summary and warning list come from the program output of that run.

# 8. Decisions

•  D32: check set (all modelling and Simscape checks, no code-generation checks); the fixes; the acceptance of the remaining warnings (proposed); Part D1 item 6 not applicable yet and item 7 open; the Step 33 files changed in this step.

# 9. Files produced

•  05_Simulink_Model/checks/: model_advisor_report.html, model_advisor_results.csv, model_advisor_accepted.csv, step34_checklist_D1.csv, step34_param_lines.csv, step34_block_numbers.csv, model_advisor_raw.mat, README.md, the three programs step34_*.m, and Transformer_Operating_Model_before_step34.slx

•  05_Simulink_Model/code_manifest_step34.sha256

•  Changed: Transformer_Operating_Model.slx, build_Transformer_Operating_Model.m, verify_step33.m, params_transformer.m and the files in results/ that verify_step33.m rewrites

# 10. What was achieved

•  Model Advisor was run on Transformer_Operating_Model.slx with 132 checks. The first run (on the Step 33 model) gave 115 passed, 16 warnings, 1 incomplete, 0 failed. After the fixes the final run gives 120 passed, 11 warnings, 1 incomplete, 0 failed; no check failed.

•  Five groups of warnings were fixed in the building program: the deprecated sqrt block, five diagnostics set to 'none', the 'bus treated as vector' setting, a hidden block name and (found by the stricter D1 scan) the zero-sequence reactance that was typed as the block default 0.5 and is now the variable X0_pu.

•  The remaining 12 results that are not 'passed' (11 warnings and 1 incomplete check) are style rules for control code, code-generation options or internals of Simscape library blocks; each has a written reason in model_advisor_accepted.csv.

•  Build Guide Part D1: 13 of 14 rows pass; D1.7 (a second person checks the build) is open and D1.6 (the app) is not applicable yet. Every dialog field of all 84 blocks was read: 245 values contain a digit and none is a typed parameter number.

•  The model still passes all nine Step 33 checks after the changes, and the 24-hour run is unchanged: K = 0.9839, top oil 78.638 degC, hot spot 100.276 degC.

# 11. Record of this step

| Item | Record |
| --- | --- |
| Step | 34 - Run the model checks |
| Environment | Claude Code (this chat) through the MATLAB MCP connection (roadmap role: Simulink Agentic Toolkit; D30) |
| Completed | 13 October 2026 |
| Status | Done; the acceptance of the remaining warnings (D32, clause 3) awaits the researcher's confirmation; D1 item 7 is open |
| Main inputs | Transformer_Operating_Model.slx (Step 33); MATLAB Build Guide Part D1; Model Advisor of Simulink Check |
| Main outputs | 05_Simulink_Model/checks/model_advisor_report.html, model_advisor_results.csv, model_advisor_accepted.csv, step34_checklist_D1.csv; corrected model and building program |
| Checks | Model Advisor: 120 passed, 11 warnings, 1 incomplete, 0 failed; Part D1: 13 of 14 rows pass (D1.7 open); verify_step33.m: 9 of 9 checks PASS; no typed parameter number in 84 blocks |
| Decisions | D32 (check set; fixes; accepted warnings proposed; D1 items 6 and 7) |

# 12. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| SW5 | The MathWorks, Inc. Simulink Check / Model Advisor, MATLAB R2025b (25.2.0.2998904). Function ModelAdvisor.run; check groups mathworks.design, mathworks.simscape, mathworks.simulink, mathworks.sl, mathworks.maab (132 checks). Use: Static model checks of Transformer_Operating_Model.slx (Step 34). | https://www.mathworks.com/help/slcheck/ref/modeladvisor.run.html |
| SW2 | MATLAB R2025b, version 25.2.0.2998904, The MathWorks, Inc., Natick, MA, USA. Use: Runs the conventional-method functions, unit tests, batch run and Duval figures (Steps 14-17). | https://www.mathworks.com/products/matlab.html |
| ST6 | IEC 60076-7:2018, Power transformers - Part 7: Loading guide for mineral-oil-immersed power transformers (Edition 2.0). The full text was NOT obtained; details TO VERIFY. Use: Basis of the top-oil and hot-spot differential equations in SS5-SS7; the thermal constants of params_transformer.m must be checked against it (TO VERIFY). |  |
| DF48 | Transformer_Operating_Model.slx, built in Step 33 by build_Transformer_Operating_Model.m from the MATLAB Build Guide Part B (decisions D30, D31); MATLAB R2025b. Use: Operating-context model: load, current, oil and hot-spot temperature, ageing. Never generates gas values (D4).. | File: 05_Simulink_Model/Transformer_Operating_Model.slx; SHA-256 FB5422C605F266DF... |
| DF52 | All parameters of the transformer operating model with unit and source (E1 pandapower, T1 Alliander). Step 33 added the constant T_zero_C_in_K = 273.15 K. Use: The only place where model values are defined; read by the model callbacks. | File: 05_Simulink_Model/params_transformer.m; SHA-256 9288320B6672E1A1... |
| DF54 | model_advisor_report.html written by ModelAdvisor.run on Transformer_Operating_Model.slx (132 checks: 120 passed, 11 warnings, 1 incomplete, 0 failed). Use: Roadmap output of Step 34 (05_Simulink_Model/checks/model_advisor_report). | File: 05_Simulink_Model/checks/model_advisor_report.html; SHA-256 5EDE8D92CF163709... |
| DF55 | model_advisor_results.csv (one row per check: id, name, status) and model_advisor_accepted.csv (the 12 non-passed checks with the number of flagged blocks and the written reason for accepting each; decision D32). Use: Evidence for the Step 34 check 'no unresolved errors remain'. | File: 05_Simulink_Model/checks/model_advisor_results.csv; SHA-256 775AC737027B2EAA... |
| DF56 | step34_checklist_D1.csv written by step34_checklist_D1.m: items D1.1-D1.5 (parameter file, typed numbers in all 84 blocks, annotations, update diagram and 24 h run against Section B12 within 0.1 K, run_transformer_simulation), D1.6 not applicable yet, D1.7 open, plus a bus test. Use: Evidence for the Step 34 roadmap check. | File: 05_Simulink_Model/checks/step34_checklist_D1.csv; SHA-256 A1E4DCAD81749018... |
| DF57 | Code written or changed in Step 34: checks/step34_run_model_advisor.m, step34_write_accepted.m, step34_checklist_D1.m; build_Transformer_Operating_Model.m, verify_step33.m, params_transformer.m (changed). Use: Fingerprints of the Step 34 code. | File: 05_Simulink_Model/code_manifest_step34.sha256; SHA-256 18D8BCC3B32990B8... |
| DF58 | Copy of Transformer_Operating_Model.slx taken before the Step 34 changes; its SHA-256 is the one that DF48 had at the end of Step 33. Use: Shows what the Step 33 model looked like; used to document the Step 34 changes. | File: 05_Simulink_Model/checks/Transformer_Operating_Model_before_step34.slx; SHA-256 1D025498C38834CB... |

# 13. How this helps the next steps

Next step: Step 35 (Simulink): verify the model against an independent solution of the IEC 60076-7 equations at rated load and in a load step from about 0.6 to 1.2 per unit; the 63 % rise time of the top-oil temperature must equal k11 times the oil time constant.

•  Step 35 verifies the model formally against an independent solution of the IEC 60076-7 equations (rated load and a load step from 0.6 to 1.2 per unit). It starts from a model that has no failed check, no open diagnostic and no typed parameter number, and whose parameter file now states unit and source for every variable.

•  Step 36 adds the operating scenarios and Step 37 the sampling-event subsystem. The checks of this step (checklist function, nine Step 33 checks, Model Advisor script) can be run again after each of them; the diagnostics now set to 'error' will stop a run that has an open connection or an Inf/NaN value.

•  The table of accepted warnings can be reused in the thesis (Chapter 3, model verification) as the record of how the model was checked.

# 14. Open items and limitations

•  The acceptance of the 12 remaining results that are not 'passed' (decision D32, clause 3) is proposed and needs the researcher's confirmation. If the supervisor wants some of the MAAB style rules satisfied (signal labels, left-to-right layout, displayed parameters), they can be added to the building program, at the cost of re-exporting the figures.

•  Build Guide D1 item 7 (a second team member checks the build against the reference script) cannot be done by a program and stays open. The automatic substitute is check 7 of verify_step33.m, which compares the model with the reference build block by block.

•  Build Guide D1 item 6 (the app runs and shows PENDING_STANDARD / NOT_CONNECTED) is not applicable yet because the dashboard belongs to Stage H; it is tested there.

•  The zero-sequence reactance X0_pu = 0.5 pu is the default of the Simscape Electrical block, not a value from the pandapower source: TO VERIFY if unbalanced cases are ever studied. It has no effect on the balanced load of this model.

•  The thermal constants are still default values of an open-source implementation, not values from IEC 60076-7:2018 (the standard was not obtained): TO VERIFY, unchanged from Step 33.

•  The Step 33 report describes the model as it was built on 12 October (5 expected differences from the reference build, 3 files with the fingerprints of that day). This step changed the model, the building program, the check program and the parameter file; the Step 33 model is kept as checks/Transformer_Operating_Model_before_step34.slx (register row DF58) and the register rows DF48, DF50 and DF52 now show the files after Step 34. The Step 33 report was not rewritten.

•  The raw result of the first Model Advisor run was overwritten by the later runs; its summary and warning list in this report are taken from the program output of that run.

•  The exact error text that the researcher saw in the earlier Simulink rerun has still not been supplied.

# 15. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| T2 | thermal fault 300 to 700 °C | Overheating in which the paper has carbonised. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| Simulink, Simscape | MATLAB's block-diagram modelling tool and its physical-modelling library | Used to model the transformer's operating conditions (Simulink Agentic Toolkit); it never makes gas values. |
| D1-D32 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| Raw and final result | Result before and after the normality gate | raw_result is what the method itself says; result is what is left after samples with low gas levels have been called Normal by the gate. |
| Unit test (matlab.unittest) | Automatic test of one small piece of code | A test that feeds a function a known input and checks the answer, so that any later change that breaks the function is noticed at once. |
| Hyperparameter grid | list of settings tried for a model | For example C and gamma of the SVM; the best combination is chosen in the inner loop (Analysis Plan 5.2). |
| NaN (not measured) | Not a Number, used here for a gas that was not measured | A marker for a missing value. It is different from 0 ppm: 0 ppm means the gas was measured and not found, NaN means nobody measured it, so no ratio or percentage can be calculated from it. |
| Applicable (method) | A method that has all the gases it needs | A method is applicable to a gas combination when every gas it uses is measured. IEC 60599 and Rogers need all five gases; Duval Triangle 1 needs CH4, C2H4 and C2H2. If a method is not applicable it answers ND for every sample. |
| Tolerance (delta) | largest acceptable loss | Fixed before the study at 0.05 macro-F1 (5 percentage points), approved in Step 4. |
| Simulink | MathWorks block-diagram simulation environment | Software in which the model is drawn as blocks and lines and simulated over time. |
| Simscape | Physical modelling extension of Simulink | Blocks that follow physical laws (electrical, thermal) and connect like real components, not like signals. |
| Subsystem (SS1-SS7) | A group of blocks shown as one block | The model is split into seven subsystems: grid, transformer, measurement, load, losses to heat, thermal network, outputs and ageing. |
| Solver Configuration | Block that sets the numerical solver of a physical network | Every physical network (the electrical one and the thermal one) needs exactly one of these blocks. |
| Annotation | Text note placed on a model diagram | A short description of what a subsystem does, its inputs, outputs and parameters, written on the diagram so that a reader does not need the code. |
| Top-oil temperature | Temperature of the oil at the top of the tank | The oil temperature used in the thermal model; it rises with load and falls back towards ambient. |
| Hot-spot temperature | Temperature of the hottest part of the winding | The winding temperature that mostly decides how fast the paper insulation ages; it is the top-oil temperature plus a load-dependent rise. |
| Load factor K | Load current divided by rated current | K = 1 means the transformer carries its rated current; K = 0.5 means half of it. |
| Relative ageing rate V | How many times faster than normal the paper ages | V = 1 at the reference hot-spot temperature (98 degC); every 6 K more doubles it. The loss of life is the sum of V over time. |
| per unit (pu) | Value divided by its rated value | A way of writing quantities so that 1.0 means rated, e.g. a current of 1.0 pu is the rated current. |
| IEC 60076-7 | IEC loading guide for oil-immersed power transformers | The standard that gives the equations for oil and hot-spot temperature and for ageing under a changing load. |
| Model Advisor | MathWorks tool that checks a Simulink model against a list of rules | A built-in inspector. It runs many checks (settings, unconnected ports, style rules) and reports each as passed, warning or failed. |
| MAAB | MathWorks Advisory Board (modelling style guidelines) | A set of style rules for control-system models. Some of them do not suit a physical plant model and are accepted with a reason. |
| Update Diagram | Simulink command that compiles the model without running it | Finds errors such as unconnected ports or wrong units before the simulation is run (Ctrl+D). |
| Zero-sequence reactance (X0) | Reactance seen by currents that are equal in all three phases | Matters only for unbalanced faults to earth; it has no effect when the three phases are loaded equally, as in this model. |