Step 35 Report

Verify against IEC 60076-7

Environment: Claude Code (this chat), MATLAB and Simulink through the MCP connection   |   Completed: 13 October 2026   |   Report version 2 (13 October 2026; regenerated after the solver tolerance was tightened)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The transformer operating model was compared with two independent solutions of the IEC 60076-7 temperature equations: a numerical solution and an exact formula. Two 24-hour tests were run: rated load from a cold start, and a load step from 0.6 to 1.2 per unit after 6 hours. After the first 10 minutes the largest difference is 0.0014 K (top oil) and 0.0129 K (hot spot) at rated load, and 0.0015 K and 0.0152 K in the load step, against the approved limit of 0.1 K. The top-oil 63.2 % rise time is 75.002 minutes against the expected 75 minutes. All 15 checks pass and the 3 October baseline is reproduced. Over the whole run, including the first minutes, the largest hot-spot difference is 0.0330 K (rated-load test), also below the limit. The solver tolerance of the model (RelTol) was tightened from 1e-3 to 1e-4 during this step, because at 1e-3 the rated-load hot-spot difference was 0.104 K, just above the limit (see Problems and fixes). This is verification: it proves that the model solves the equations with its constants, not that the constants are those of IEC 60076-7:2018, which are still TO VERIFY.

# 1. Purpose of this step

Before the model is used for scenarios, we must know that it does what its equations say. This step runs the model in two tests and compares its temperatures with calculations that do not use the Simscape model, and it produces Table 4.10 and Figure 4.18 of the thesis.

# 2. Method used

## Approach

Verification means asking: does the model solve the equations it claims to solve? The model was run for 24 hours in two tests, and its top-oil and hot-spot temperatures were compared, point by point, with calculations that do not use the Simscape model at all.

Reference A solves the IEC 60076-7 differential equations (Equations 1 to 4 below) with a numerical solver (ode15s, very tight tolerances), using the load factor K(t) that the model itself measured. Reference B (rated-load test only) uses the exact formula that the same equations give for a constant load (Equation 5), so it needs no solver at all. Reference A was also compared with reference B, to show that the reference itself is accurate.

Test 1 is rated load from a cold start (all temperatures equal to the ambient 20 degC). Test 2 is a load step from 0.6 to 1.2 per unit after 6 hours. Two further checks were made: the time for the top-oil rise to reach 63.2 % must equal k11 times the oil time constant (75 minutes), and the ageing rate V must follow its formula for the reference hot-spot temperature. The numbers of the 3 October reference build were reproduced as a baseline.

## Why this method

•  Comparing a model with an independent solution of its own equations is the standard way to verify (not validate) a simulation model: it shows that the blocks were assembled correctly and that the numerical settings are adequate.

•  Two independent references, one numerical and one exact, protect against a mistake in either of them: they agree to better than a billionth of a kelvin for the top oil, so any difference to the model is the model's.

•  Excluding the first 10 minutes follows the approved Analysis Plan (Equation 45) and the 3 October baseline; the start-up transient is reported separately and openly.

•  The 63 % rise time is a sharp test of the oil time constant, because it depends only on k11 and tau_o and on the thermal capacity and resistance chosen in the model.

## Settings and rules

| Setting | Value |
| --- | --- |
| Tests | Test 1: rated demand, cold start, 24 h. Test 2: demand 0.6 pu, then 1.2 pu after 6 h (1 s ramp), 24 h |
| Reference A | ode15s, relative and absolute tolerance 1e-8, maximum step 30 s, driven by the model's measured K(t) |
| Reference B | closed form for constant K (Test 1 only; K = mean of the logged K after 1 h) |
| Solver | ode23t, RelTol 1e-4 (variable solver_reltol), maximum step 60 s |
| Compared points | the model's own logged time points after 600 s (10 min), reference evaluated there: 1446 in Test 1, 1523 in Test 2 |
| Tolerance | e_max <= 0.1 K for top-oil and hot-spot temperature in both tests (approved, Analysis Plan Section 9) |
| Rise-time criterion | 63.2 % (1 - 1/e) of the analytic steady-state oil rise; within 1 min of k11 x tau_o (decision D33) |
| Ageing-rate criterion | relative difference <= 2^(0.1/6) - 1 = 1.16 % (the ageing rate that 0.1 K causes; D33) |
| Software | MATLAB 25.2.0.2998904 (R2025b), Simulink, Simscape, Simscape Electrical |

## Equations

k11τodθodt=1+K2R1+RxΔθor-θo-θa#1

where:

θo  –  top-oil temperature, °C

θa  –  ambient temperature, °C (20 °C)

t  –  time, s (the equation holds in any consistent time unit)

k11, τo  –  oil thermal-model constant (0.5) and oil time constant (150 min)

K  –  load factor, per unit

R  –  ratio of load loss at rated current to no-load loss (P_k / P_0), dimensionless

x  –  oil exponent (0.8)

Δθor  –  top-oil rise above ambient at rated load, K (60 K)

k22τwdΔθh1dt=k21ΔθhrKy-Δθh1#2

where:

Δθh1  –  first component of the hot-spot-to-top-oil gradient, K

k21, k22  –  winding thermal-model constants (both 2)

τw  –  winding time constant (7 min)

Δθhr  –  hot-spot-to-top-oil gradient at rated load, K (hot-spot factor times winding gradient)

y  –  winding exponent (1.3)

τok22dΔθh2dt=k21-1ΔθhrKy-Δθh2#3

where:

Δθh2  –  second component of the hot-spot-to-top-oil gradient, K

all other symbols as in the two equations above.

θh=θo+Δθh1-Δθh2#4

where:

θ  –  _

h  –  o

θot=θa+Δθo,∞1-e-tk11τo#5

where:

Δθo,∞  –  steady-state top-oil rise for the constant K, K = [(1+K^2 R)/(1+R)]^x Δθ_"or"

the two winding components follow the same exponential form with their own time constants k_22 τ_w and τ_o / k_22 (closed form B).

emax=maxtθsimt-θreft,    RMSE=1Mm=1Mθsimtm-θreftm2#6

where:

emax  –  largest absolute difference between model and reference, K

θsim, θref  –  temperature from the Simulink model and from the reference, °C

tm, M  –  the compared time points (after 10 min) and their number

RMSE  –  root-mean-square difference, K

## Tools and programs

•  05_Simulink_Model/verify_step35.m (runs both tests, both references, 15 checks, Table 4.10, Figure 4.18, SDI session)

•  MATLAB ode15s; Simulink.SimulationInput; Simulink.sdi (Simulation Data Inspector); exportgraphics

•  Colours and line styles read from 11_Results/figures/plot_style.csv (never typed)

•  00_Project_Admin/report_builder/update_register_step35.ps1 (register, glossary)

## Method references

[ST6] IEC 60076-7:2018, Power transformers - Part 7: Loading guide for mineral-oil-immersed power transformers (Edition 2.0). The full text was NOT obtained; details TO VERIFY.

[SW4] Alliander N.V., transformer-thermal-model (IEC 60076-7 implementation, MPL-2.0), file transformer_thermal_model/transformer/power.py, class PowerTransformer, ONAF default specifications (source T1 of the Build Guide). https://github.com/alliander-opensource/transformer-thermal-model

[DF53] Transformer_Operating_Model.slx built by reference_build/build_transformer_model.m and re-run on 11 October 2026; used in Step 33 as the structure and result reference. The Step 33 model is compared with it block by block.

# 3. What was used

•  Transformer_Operating_Model.slx as after Step 34 and params_transformer.m.

•  The IEC 60076-7 equations as written in the MATLAB Build Guide (Section A3.2) and the Analysis Plan (Section 9, Equations 40 to 46).

•  The numbers of the 3 October reference build (verification_log_2026-10-03.txt) as a baseline.

•  11_Results/figures/plot_style.csv for the colours of Figure 4.18.

# 4. What was done, step by step

1.  Fixed the test design, the measures and the extra criteria in the decision log (D33) before running anything.

2.  Wrote verify_step35.m: it runs the two tests, solves reference A and calculates reference B, measures e_max and RMSE after 10 minutes, finds the 63.2 % rise time, runs 15 checks, writes Table 4.10, draws Figure 4.18 and saves the runs in the Simulation Data Inspector.

3.  Ran it. All checks passed at the first run; the first figure had dark axes (see Problems and fixes), and the whole-run start-up difference was added to the log.

4.  After Step 37 added the sampling-event subsystem the program was run again on the final model. The Test 1 hot-spot difference was then 0.104 K, above the 0.1 K limit, with the model physics unchanged. The cause was found to be the solver accuracy (RelTol 1e-3); the tolerance was set to 1e-4 (variable solver_reltol in params_transformer.m), the model was rebuilt, and all verification steps were repeated (D33 amendment).

5.  Wrote this version of the report (version 2) and updated the register, glossary, READMEs, CHANGELOG.md and SESSION_SUMMARY.md.

# 5. What we found

## Table 4.10 - Simulink verification

| Test | Quantity and measure | Value | Unit | Limit | Result |
| --- | --- | --- | --- | --- | --- |
| Test 1 rated load | top-oil temperature: e_max (after 10 min) | 0.0014 | K | 0.1000 | pass |
| Test 1 rated load | hot-spot temperature: e_max (after 10 min) | 0.0129 | K | 0.1000 | pass |
| Test 1 rated load | top-oil temperature: RMSE (after 10 min) | 0.0002 | K | - |  |
| Test 1 rated load | hot-spot temperature: RMSE (after 10 min) | 0.0007 | K | - |  |
| Test 1 rated load | top-oil temperature: final value, model | 78.638 | degC | - |  |
| Test 1 rated load | hot-spot temperature: final value, model | 100.276 | degC | - |  |
| Test 1 rated load | hot-spot temperature: peak value, model | 100.276 | degC | - |  |
| Test 1 rated load | ageing rate V: largest relative difference | 0.0015 | - | 0.0116 | pass |
| Test 1 rated load | top-oil temperature: legacy measure (information) | 0.0023 | K | - |  |
| Test 1 rated load | hot-spot temperature: legacy measure (information) | 0.0234 | K | - |  |
| Test 1 rated load | top-oil temperature: interpolation error of the logged grid (information) | 0.0009 | K | - |  |
| Test 1 rated load | hot-spot temperature: interpolation error of the logged grid (information) | 0.0109 | K | - |  |
| Test 2 load step | top-oil temperature: e_max (after 10 min) | 0.0015 | K | 0.1000 | pass |
| Test 2 load step | hot-spot temperature: e_max (after 10 min) | 0.0152 | K | 0.1000 | pass |
| Test 2 load step | top-oil temperature: RMSE (after 10 min) | 0.0002 | K | - |  |
| Test 2 load step | hot-spot temperature: RMSE (after 10 min) | 0.0013 | K | - |  |
| Test 2 load step | top-oil temperature: final value, model | 95.496 | degC | - |  |
| Test 2 load step | hot-spot temperature: final value, model | 122.700 | degC | - |  |
| Test 2 load step | hot-spot temperature: peak value, model | 122.700 | degC | - |  |
| Test 2 load step | ageing rate V: largest relative difference | 0.0018 | - | 0.0116 | pass |
| Test 2 load step | top-oil temperature: legacy measure (information) | 0.0020 | K | - |  |
| Test 2 load step | hot-spot temperature: legacy measure (information) | 0.0286 | K | - |  |
| Test 2 load step | top-oil temperature: interpolation error of the logged grid (information) | 0.0008 | K | - |  |
| Test 2 load step | hot-spot temperature: interpolation error of the logged grid (information) | 0.0144 | K | - |  |
| Test 1 rated load | top-oil temperature: e_max against closed form B | 0.0014 | K | 0.1000 | pass |
| Test 1 rated load | hot-spot temperature: e_max against closed form B | 0.0129 | K | 0.1000 | pass |
| Test 1 rated load | top-oil temperature: 63.2 % rise time (difference to k11 x tau_o) | 0.0016 | min | 1.0000 | pass |

'After 10 min' means the 1446 (Test 1) and 1523 (Test 2) logged model time points after 600 s (the references are evaluated at the model's own time points). 'Closed form B' is the exact formula for a constant load; the rise-time row gives the difference between the model's 63.2 % time (75.002 min) and k11 x tau_o = 75.000 min. The ageing-rate row is the largest relative difference between the model's ageing rate and the formula applied to the reference hot-spot temperature.

## Figure 4.18

Figure 4.18  Verification of the Simulink thermal model: temperatures (upper panels) and model minus reference (lower panels) for the rated-load test and the load-step test

The solid lines (model) lie on top of the dashed lines (IEC 60076-7 equations). The lower panels show the difference in kelvin; the dotted lines are the tolerance of 0.1 K. All differences are far below the tolerance; the largest occur in the first minutes after the start.

## Start-up transient

Over the whole run, the largest hot-spot difference in Test 1 is 0.0330 K, at 85 s; it never exceeds 0.1 K. In Test 2 the whole-run maximum is 0.0337 K. The top-oil difference never exceeds 0.1 K in either test. The approved rule (Equation 45) compares from 10 minutes onwards, as in the 3 October baseline; the whole-run values are reported because a reader of the figure will see the early difference. They are about two to three times the values after 10 minutes, which is what a start-up transient with a changing load factor produces.

## Baseline of 3 October

| Quantity | 3 October baseline | This step |
| --- | --- | --- |
| Test 1: load factor K | 0.9839 | 0.9839 |
| Test 1: final top-oil temperature (degC) | 78.638 | 78.638 |
| Test 1: final hot-spot temperature (degC) | 100.276 | 100.276 |
| Test 1: top-oil 63 % rise time (min) | 75.0 | 75.002 |
| Test 2: load factor before / after the step | 0.5960 / 1.1733 | 0.5960 / 1.1733 |
| Test 2: final hot-spot temperature (degC) | 122.70 | 122.700 |

The model of Step 33/34 therefore reproduces the verified reference build, as the structure check of Step 33 already showed.

# 6. Checks

| Check (verify_step35.m) | Value | Limit | Result |
| --- | --- | --- | --- |
| Test 1: top-oil e_max against reference A (K) | 1.4162E-3 | 0.1000 | PASS |
| Test 1: hot-spot e_max against reference A (K) | 1.2898E-2 | 0.1000 | PASS |
| Test 2: top-oil e_max against reference A (K) | 1.4890E-3 | 0.1000 | PASS |
| Test 2: hot-spot e_max against reference A (K) | 1.5162E-2 | 0.1000 | PASS |
| Test 1: top-oil e_max against closed form B (K) | 1.4162E-3 | 0.1000 | PASS |
| Test 1: hot-spot e_max against closed form B (K) | 1.2898E-2 | 0.1000 | PASS |
| reference A equals closed form B, top-oil (K) | 4.9962E-10 | 0.0010 | PASS |
| reference A equals closed form B, hot-spot (K) | 7.4233E-8 | 0.0010 | PASS |
| top-oil 63.2 % rise time equals k11*tau_o (difference, min) | 1.5984E-3 | 1.0000 | PASS |
| ageing rate V equals formula on reference hot-spot, Test 1 (relative) | 1.4889E-3 | 0.0116 | PASS |
| ageing rate V equals formula on reference hot-spot, Test 2 (relative) | 1.7501E-3 | 0.0116 | PASS |
| Test 1 final top-oil equals 3 Oct baseline (K) | 4.7666E-4 | 0.1000 | PASS |
| Test 1 final hot-spot equals 3 Oct baseline (K) | 2.1675E-4 | 0.1000 | PASS |
| Test 2 load factor before the step equals baseline (pu) | 2.9579E-5 | 0.0005 | PASS |
| Test 2 load factor after the step equals baseline (pu) | 1.9284E-5 | 0.0005 | PASS |

# 7. Problems and fixes

•  The first version of Figure 4.18 had black axes, apparently because the default theme of MATLAB R2025b was applied to the invisible figure. The program now forces the light theme and a white axes colour; the figure was looked at again.

•  After Step 37 the Test 1 hot-spot difference after 10 minutes was 0.104 K (limit 0.1 K) although the model had not changed. A first explanation (interpolation on a changed time grid) was wrong. Tests with other solver tolerances showed that the default RelTol 1e-3 leaves an error of about 0.1 K that depends on the solver steps; RelTol 1e-4 gives 0.013 K (run time about 63 s). The model now uses 1e-4. The first wording of the D33 amendment was corrected in the decision log.

•  The first run did not log when the largest difference occurs; a start-up line was added to the log before this report was written.

# 8. Decisions

•  D33: two references (numerical and closed form), two tests, e_max and RMSE after 10 minutes, the 0.1 K limit, the rise-time and ageing-rate criteria (proposals), and the use of the model's measured K for the reference. Fixed before the program was run. Amended on 13 October 2026 after the Step 37 run: the references are evaluated at the model's own logged time points, and the solver tolerance of the model is 1e-4 (the cause of the 0.104 K result).

# 9. Files produced

•  05_Simulink_Model/verify_step35.m, code_manifest_step35.sha256

•  05_Simulink_Model/results/step35_verification_log_2026-10-13.txt, step35_checks.csv, step35_sdi_session.mldatx

•  11_Results/tables/T4_10_simulink_verification.csv

•  11_Results/figures/F4_18_simulink_verification.png, .pdf and .csv (the plotted numbers)

# 10. What was achieved

•  The model was verified against two independent solutions of the IEC 60076-7 equations in two 24-hour tests; all 15 checks pass (decision D33).

•  Largest difference after 10 minutes: top-oil 0.0014 K and hot-spot 0.0129 K at rated load; 0.0015 K and 0.0152 K in the load step; the limit is 0.1 K.

•  The top-oil 63.2 % rise time is 75.002 min against k11 x tau_o = 75.000 min.

•  The numbers of the 3 October baseline are reproduced: K 0.9839, final top-oil 78.638 degC and hot-spot 100.276 degC (rated load); 122.700 degC hot-spot after the step.

•  Table 4.10 and Figure 4.18 were produced, and both runs were stored in a Simulation Data Inspector session.

# 11. Record of this step

| Item | Record |
| --- | --- |
| Step | 35 - Verify against IEC 60076-7 |
| Environment | Claude Code (this chat) through the MATLAB MCP connection (roadmap role: Simulink Agentic Toolkit; D30) |
| Completed | 13 October 2026 |
| Status | Done |
| Main inputs | Transformer_Operating_Model.slx (as after Step 34); params_transformer.m; Analysis Plan Section 9 |
| Main outputs | results/step35_verification_log_2026-10-13.txt, step35_checks.csv, step35_sdi_session.mldatx; 11_Results/tables/T4_10_simulink_verification.csv; 11_Results/figures/F4_18_simulink_verification.(png¦pdf¦csv) |
| Checks | verify_step35.m: 15 of 15 checks PASS; e_max after 10 min 0.1 K limit: 0.0014 / 0.0129 K (Test 1), 0.0015 / 0.0152 K (Test 2); 63 % rise time 75.002 min |
| Decisions | D33 (test design, measures, additional criteria; amendment of 13 October 2026) |

# 12. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| ST6 | IEC 60076-7:2018, Power transformers - Part 7: Loading guide for mineral-oil-immersed power transformers (Edition 2.0). The full text was NOT obtained; details TO VERIFY. Use: Basis of the top-oil and hot-spot differential equations in SS5-SS7; the thermal constants of params_transformer.m must be checked against it (TO VERIFY). |  |
| SW4 | Alliander N.V., transformer-thermal-model (IEC 60076-7 implementation, MPL-2.0), file transformer_thermal_model/transformer/power.py, class PowerTransformer, ONAF default specifications (source T1 of the Build Guide). Use: Default thermal constants of params_transformer.m (dTheta_or, g_r, H, tau_o, tau_w, k11, k21, k22, x, y) and the form of the thermal differential equations. | https://github.com/alliander-opensource/transformer-thermal-model |
| DF48 | Transformer_Operating_Model.slx, built in Step 33 by build_Transformer_Operating_Model.m from the MATLAB Build Guide Part B (decisions D30, D31); MATLAB R2025b. Use: Operating-context model: load, current, oil and hot-spot temperature, ageing. Never generates gas values (D4).. | File: 05_Simulink_Model/Transformer_Operating_Model.slx; SHA-256 FB5422C605F266DF... |
| DF52 | All parameters of the transformer operating model with unit and source (E1 pandapower, T1 Alliander). Step 33 added the constant T_zero_C_in_K = 273.15 K. Use: The only place where model values are defined; read by the model callbacks. | File: 05_Simulink_Model/params_transformer.m; SHA-256 9288320B6672E1A1... |
| DF53 | Transformer_Operating_Model.slx built by reference_build/build_transformer_model.m and re-run on 11 October 2026; used in Step 33 as the structure and result reference. The Step 33 model is compared with it block by block. Use: Reference for the Step 33 structure check. | File: 05_Simulink_Model/reference_build/rerun_2026-10-11/Transformer_Operating_Model.slx; SHA-256 E7813F90454B4160... |
| DF59 | Written by verify_step35.m: two 24 h tests (rated load; load step 0.6 to 1.2 pu at 6 h) compared with the IEC 60076-7 equations (ode15s reference and closed form), 15 checks (decision D33). Use: Evidence for the Step 35 roadmap check. | File: 05_Simulink_Model/results/step35_verification_log_2026-10-13.txt; SHA-256 C7784E4248CBC0FD... |
| DF60 | Largest difference (e_max), RMSE, final and peak values and ageing-rate difference of the model against the IEC 60076-7 equations, both tests, with the approved limits. Use: Table 4.10 of the thesis. | File: 11_Results/tables/T4_10_simulink_verification.csv; SHA-256 432A33B80CE9F98E... |
| DF61 | Four panels (temperatures; model minus reference) for both tests; colours from 11_Results/figures/plot_style.csv. Also .pdf and the plotted numbers (.csv) in the same folder. Use: Figure 4.18 of the thesis. | File: 11_Results/figures/F4_18_simulink_verification.png; SHA-256 0EFD9C6C10DB69CD... |
| DF62 | Both verification runs (K_pu, theta_oil_C, theta_hs_C, ageing_rate_V) saved with Simulink.sdi.save. Use: Logged signals behind Figure 4.18 (roadmap: Simulation Data Inspector logs). | File: 05_Simulink_Model/results/step35_sdi_session.mldatx; SHA-256 EB3D86CDD100949F... |
| DF63 | verify_step35.m (new in Step 35). Use: Fingerprint of the Step 35 code. | File: 05_Simulink_Model/code_manifest_step35.sha256; SHA-256 39415689CB713987... |

# 13. How this helps the next steps

Next step: Step 36 (Simulink): write the approved operating scenarios in scenarios.m (constant rated load, a daily load cycle, a short overload), simulate each, log load, temperatures and ageing in the Simulation Data Inspector, and draw Figure 4.19.

•  Step 36 runs the approved operating scenarios (constant rated load, a daily load cycle, a short overload) on a model whose thermal and ageing chain now agrees with the IEC 60076-7 equations to within 0.1 K. Its figures (Figure 4.19) can be read as the equations' answer for those loads.

•  Step 37 added the sampling-event subsystem; the verification program was run again on the final model and passes, so the temperatures are those of the equations.

•  Chapter 3 can state the verification result with Table 4.10 and Figure 4.18, together with the limits below.

# 14. Open items and limitations

•  The verification shows that the model solves the equations with the constants in params_transformer.m. It does not show that those constants are right: they are default values of an open-source implementation, not values from IEC 60076-7:2018 (not obtained) or a test report: TO VERIFY. No measured temperatures of a real transformer were used, so this is verification, not validation.

•  Over the whole run the hot-spot temperature differs from the reference by up to 0.0330 K (at 85 s, in the first minutes); the approved rule compares from 10 minutes onwards. The reference is driven by the logged load factor, which changes fast in the first seconds. The result depends on the solver tolerance: with RelTol 1e-3 the Test 1 difference after 10 minutes was 0.104 K, above the limit; with 1e-4 it is well below. A user who loosens the tolerance must repeat this verification.

•  The reference is driven by the model's own measured load factor, so the electrical network that produces K is not tested here; it was compared with the reference build and with the steady-state calculation in Step 33.

•  The tolerances for the rise time (1 min) and the ageing rate (1.16 %) are proposals of decision D33; the 0.1 K tolerance is the approved one.

•  The Simulation Data Inspector session is a binary file whose hash changes with every save.

•  The researcher's error text from the earlier Simulink rerun has still not been supplied.

# 15. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| Simulink, Simscape | MATLAB's block-diagram modelling tool and its physical-modelling library | Used to model the transformer's operating conditions (Simulink Agentic Toolkit); it never makes gas values. |
| D1-D34 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| Hyperparameter grid | list of settings tried for a model | For example C and gamma of the SVM; the best combination is chosen in the inner loop (Analysis Plan 5.2). |
| NaN (not measured) | Not a Number, used here for a gas that was not measured | A marker for a missing value. It is different from 0 ppm: 0 ppm means the gas was measured and not found, NaN means nobody measured it, so no ratio or percentage can be calculated from it. |
| Tolerance (delta) | largest acceptable loss | Fixed before the study at 0.05 macro-F1 (5 percentage points), approved in Step 4. |
| Simulink | MathWorks block-diagram simulation environment | Software in which the model is drawn as blocks and lines and simulated over time. |
| Simscape | Physical modelling extension of Simulink | Blocks that follow physical laws (electrical, thermal) and connect like real components, not like signals. |
| Subsystem (SS1-SS7) | A group of blocks shown as one block | The model is split into seven subsystems: grid, transformer, measurement, load, losses to heat, thermal network, outputs and ageing. |
| Top-oil temperature | Temperature of the oil at the top of the tank | The oil temperature used in the thermal model; it rises with load and falls back towards ambient. |
| Hot-spot temperature | Temperature of the hottest part of the winding | The winding temperature that mostly decides how fast the paper insulation ages; it is the top-oil temperature plus a load-dependent rise. |
| Load factor K | Load current divided by rated current | K = 1 means the transformer carries its rated current; K = 0.5 means half of it. |
| Relative ageing rate V | How many times faster than normal the paper ages | V = 1 at the reference hot-spot temperature (98 degC); every 6 K more doubles it. The loss of life is the sum of V over time. |
| per unit (pu) | Value divided by its rated value | A way of writing quantities so that 1.0 means rated, e.g. a current of 1.0 pu is the rated current. |
| IEC 60076-7 | IEC loading guide for oil-immersed power transformers | The standard that gives the equations for oil and hot-spot temperature and for ageing under a changing load. |
| Simulation Data Inspector (SDI) | MathWorks tool that stores and compares logged simulation signals | A viewer in which the signals of each run are kept, so runs can be compared or saved as a session file. |
| e_max (largest difference) | Largest absolute difference between model and reference over the compared time points | The worst-case error of the model, in kelvin. It must stay within 0.1 K. |
| RMSE (root-mean-square error) | Square root of the mean of the squared differences | A typical size of the error over the whole run, less sensitive to a single worst point than the largest difference. |
| Closed-form solution | Exact formula for the answer, with no numerical solver | For a constant load the oil and winding temperatures follow simple exponential curves; this formula is an independent check of the model and of the numerical reference. |
| 63 % rise time | Time for a first-order quantity to reach 63.2 % (1 - 1/e) of its final change | For the top-oil temperature this time equals the oil time constant times k11, i.e. 75 minutes here. |
| Overload | Load above rated current | A load factor above 1.0 per unit; the hot spot heats quickly and the ageing rate rises steeply. |
| Operating scenario | A chosen load history used to run the model | An illustrative example of how the transformer is loaded over time (constant, daily cycle, overload); it is not measured data. |