Step 37 Report

Add the DGA sampling-event subsystem

Environment: Claude Code (this chat), MATLAB and Simulink through the MCP connection   |   Completed: 13 October 2026   |   Report version 1 (13 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: A new subsystem, SS8, was added to the transformer operating model. At the sampling times 6, 12, 18, 22 h it counts the sampling events (record_index) and raises a 60 s pulse (sampling_event). It has no input and no output port, so it cannot affect the temperatures, and it contains only 13 clock, constant, comparison, counting, logic and logging blocks: it cannot produce a gas value. The text record_id of the next held-out record is looked up outside the model, in dga_master.csv, from the index. All 10 checks pass, including the test that no block, name, value or logged signal refers to a gas, and the test that the temperatures of the three Step 36 scenarios are unchanged (largest difference 0.0021 K on the common time points). A Step 35 check that failed after SS8 was added (0.104 K against 0.1 K) was traced to the solver tolerance, not to SS8, and fixed (RelTol 1e-4). The sampling times are illustrative.

# 1. Purpose of this step

The operating-context model must be able to say when a gas sample would be taken, so that the dashboard can show the real measured record at that moment. The model must never create a gas concentration (decision D4). This step adds the event generator, and tests that it generates events only.

# 2. Method used

## Approach

Event generation without data: a sampling event is a moment in simulated time at which a laboratory sample would be taken. Subsystem SS8 knows only the list of sampling times (params_transformer.m) and the simulation clock. It counts how many sampling times have passed and raises a one-minute pulse after each of them. It has no input and no output port, so nothing can flow from it into the temperature and ageing subsystems SS1 to SS7.

A Simulink signal is a number, not text. SS8 therefore outputs record_index, the number of sampling times passed (0 before the first, then 1, 2, ...). The text identifier of the record (record_id) is looked up outside the model, by get_sampling_events.m, in a list of held-out record identifiers that params_transformer.m reads from dga_master.csv. Only two columns of that file are read, record_id and data_role, so no gas value ever enters the model's workspace.

Held-out means every record of dga_master.csv whose data_role is not development (benchmark, internal test and external test; 388 records), in file order: the k-th sampling event takes the k-th of them (decision D35). The requirement that no block produces a gas concentration is tested, not assumed: the test inspects every block, every name and dialog value, the logged signals and the code that reads the file.

## Why this method

•  The framework must show, in the operating context, WHEN a gas sample would be taken, so that the dashboard can pick up the real measured record at that moment. The model must never invent a gas concentration (decision D4); the records come from measurements only.

•  Using a count of sampling times instead of text keeps the subsystem to clock, comparison, counting and logic blocks, which can be inspected completely.

•  Because SS8 is not connected to SS1-SS7, adding it must not change the temperatures. This is tested against the saved Step 36 results. It does change the solver time grid slightly, because the solver has to stop at each sampling time; the test therefore compares the signals on the time points that both runs share.

## Settings and rules

| Setting | Value |
| --- | --- |
| Sampling times | t_sample_h = 6, 12, 18, 22 h (illustrative; params_transformer.m) |
| Event pulse | t_event_s = 60 s after each sampling time |
| Held-out records | 388 records of dga_master.csv with data_role not development; only the columns record_id and data_role are read |
| Logged signals of SS8 | record_index (0, 1, 2, ...) and sampling_event (0 or 1) |
| Solver | ode23t, RelTol 1e-4 (variable solver_reltol), maximum step 60 s (the tolerance was tightened in Step 35, D33) |
| Software | MATLAB 25.2.0.2998904 (R2025b), Simulink, Simscape, Simscape Electrical |

## Equations

kt=j=1nHt-tj#1

where:

kt  –  record_index: the number of sampling times passed at time t, dimensionless

H  –  unit step: 0 for a negative argument and 1 otherwise

tj  –  the j-th sampling time, s (t_sample_h x 3600)

n  –  number of sampling times (4)

## Tools and programs

•  05_Simulink_Model/verify_step37.m (10 checks: inspection, timing, record ids, regression, Step 33 checks)

•  05_Simulink_Model/get_sampling_events.m (looks up record_id from record_index); params_transformer.m (sampling times, held-out list)

•  05_Simulink_Model/build_Transformer_Operating_Model.m (builds SS8 and sets solver_reltol)

•  00_Project_Admin/report_builder/update_register_step37.ps1 (register, glossary)

## Method references

[ST6] IEC 60076-7:2018, Power transformers - Part 7: Loading guide for mineral-oil-immersed power transformers (Edition 2.0). The full text was NOT obtained; details TO VERIFY.

[SW4] Alliander N.V., transformer-thermal-model (IEC 60076-7 implementation, MPL-2.0), file transformer_thermal_model/transformer/power.py, class PowerTransformer, ONAF default specifications (source T1 of the Build Guide). https://github.com/alliander-opensource/transformer-thermal-model

[DF2] Made in Step 9 from DS1-DS5 (Steps 5-9 programs).

# 3. What was used

•  The model Transformer_Operating_Model.slx of Steps 33 to 36 and params_transformer.m.

•  03_Data/processed/dga_master.csv, only the columns record_id and data_role (the role says whether a record is development, benchmark, internal test or external test).

•  The saved Step 36 results (kept in results/before_step37/) for the regression test.

# 4. What was done, step by step

1.  Fixed the design and the tests in the decision log (D35) before building: what held-out means, how the sampling times are set, and how a text identifier can leave a numeric model.

2.  Added the sampling times, the pulse length and the held-out list to params_transformer.m (only two columns of the CSV are read), wrote get_sampling_events.m, and built SS8 in build_Transformer_Operating_Model.m.

3.  Wrote verify_step37.m with 10 checks. During the build the first amendment of D35 was made: the solver time grid changes slightly when SS8 is added, so the thermal signals can be compared with the saved ones only on the common time points (within 0.01 K), not point by point.

4.  Re-running the Step 35 verification on the model with SS8 gave a hot-spot difference of 0.104 K in Test 1 against the limit 0.1 K, although SS8 is not connected to the thermal network. A first explanation (interpolation on a different grid) was incomplete. Tests of the solver tolerance showed that the default RelTol 1e-3 leaves an error of about 0.1 K that moves with the solver steps; RelTol 1e-4 gives 0.013 K. The tolerance is now the variable solver_reltol in params_transformer.m (D33 and D35 amendments).

5.  Rebuilt the model and repeated Steps 33, 35, 36 and 37 and the Model Advisor and checklist of Step 34 on the final model; the regression test of check 9 is run at the old tolerance (1e-3) so that it measures only the effect of SS8.

6.  Wrote this report and updated the register, glossary, READMEs, CHANGELOG.md and SESSION_SUMMARY.md.

# 5. What we found

## The subsystem

| Block of SS8 | Kind |
| --- | --- |
| Event_AND | Logic |
| Index_to_Boolean | DataTypeConversion |
| Last_Sample_Time | MinMax |
| Log_record_index | ToWorkspace |
| Log_sampling_event | ToWorkspace |
| Pick_Times | Product |
| Record_Index_Sum | Sum |
| Sample_Times | Constant |
| Time | Clock |
| Time_Passed | RelationalOperator |
| Time_Since_Sample | Sum |
| To_Double | DataTypeConversion |
| Within_Pulse | Compare To Constant |

Every block is a clock, a constant, a comparison, a counting or logic block, or a logging block. SS8 has no input port and no output port; its two logged signals, record_index and sampling_event, go only to the workspace.

## Sampling events

| Sampling time (h) | record_index | record_id (looked up outside the model) |
| --- | --- | --- |
| 6.0 | 1 | IECTC10_0001 |
| 12.0 | 2 | IECTC10_0002 |
| 18.0 | 3 | IECTC10_0003 |
| 22.0 | 4 | IECTC10_0004 |

The four identifiers are the first four held-out records of dga_master.csv (role benchmark). The sampling times are illustrative and can be replaced in params_transformer.m.

# 6. Checks

| Check (verify_step37.m) | Result |
| --- | --- |
| SS8 has an annotation and a Description, and no input or output port (no connection to SS1-SS7) | PASS |
| every block of SS8 is a clock, constant, comparison, counting, logic or logging block | PASS |
| no block name or dialog value in the model refers to a gas or a concentration | PASS |
| the logged signals are exactly K_pu, theta_oil_C, theta_hs_C, ageing_rate_V, record_index, sampling_event | PASS |
| params_transformer.m reads only the columns record_id and data_role and defines no gas variable | PASS |
| record_index is 0 before the first sampling time and k from the k-th (step within 1e-6 s) | PASS |
| sampling_event is 1 only inside [t_k, t_k + t_event_s) and one pulse per sampling time | PASS |
| the record_ids are the first held-out ids, unique, and exist in dga_master.csv with a role other than development | PASS |
| Step 36 scenarios: same signals as the saved results on common time points (0.01 K; K 1e-4; V 0.12 %) | PASS |
| the nine checks of verify_step33.m pass on the model with SS8 | PASS |

Check 9 compares the thermal and ageing signals of the three Step 36 scenarios with the saved results on the time points that both runs share: rated: 296 common points of 1441; oil 0.0021 K, hot-spot 0.0021 K, K 6.7e-16, V 2.40e-04 | daily: 295 common points of 4322; oil 0.0009 K, hot-spot 0.0009 K, K 1.7e-16, V 1.02e-04 | overload: 296 common points of 1475; oil 0.0015 K, hot-spot 0.0015 K, K 4.4e-16, V 1.78e-04. The limit is 0.01 K. Check 10 repeats the nine checks of Step 33 on the model with SS8.

# 7. Problems and fixes

•  The solver time grid changes when SS8 is added, so the signals could not be compared point by point with the saved ones. The comparison was changed to the common time points (amendment of D35, logged openly).

•  After SS8 was added the Step 35 hot-spot difference after 10 minutes rose to 0.104 K (limit 0.1 K). The cause was the solver accuracy; RelTol 1e-3 was changed to 1e-4 (0.013 K, run time about 63 s) and all verification steps were repeated. The first explanation, written in the decision log, was corrected.

•  The first regression check, run after the tolerance change, failed (hot-spot differences of 0.026 K and 0.060 K on only four to five common points) because the saved results were produced at the old tolerance. The check now runs at that tolerance, so that only SS8 is compared (296 common points).

•  A tool message 'Dot indexing is not supported for variables of this type' appears in the Model Advisor run; it belongs to the check na_0030, which was already recorded as incomplete in D32 and replaced by the direct test that the model has no bus.

# 8. Decisions

•  D35: held-out records (role not development, 388, in file order); sampling times and pulse in params_transformer.m; record_index and sampling_event as the numeric outputs; only two CSV columns read; the tests; the regression rule (common points, 0.01 K). Two amendments.

•  D33 amendment: the solver tolerance of the model is 1e-4.

# 9. Files produced

•  05_Simulink_Model/Transformer_Operating_Model.slx (with SS8), build_Transformer_Operating_Model.m, params_transformer.m, get_sampling_events.m, verify_step37.m, code_manifest_step37.sha256

•  05_Simulink_Model/results/step37_checks.csv, step37_sampling_events.csv, step37_ss8_blocks.csv

•  05_Simulink_Model/results/before_step37/ (the Step 36 results before SS8, used by check 9)

# 10. What was achieved

•  Subsystem SS8 (sampling events) was added to the model. At the sampling times 6, 12, 18, 22 h it raises record_index and a 60 s event pulse; it has no connection to SS1-SS7 (decision D35).

•  All 10 checks of verify_step37.m pass, including: no block, name, value or logged signal refers to a gas or a concentration; params_transformer.m reads only record_id and data_role; the index steps at the set times to within 1e-6 s.

•  The first four held-out records are IECTC10_0001, IECTC10_0002, IECTC10_0003, IECTC10_0004; they exist in dga_master.csv with the role benchmark.

•  The thermal and ageing signals of the three Step 36 scenarios agree with the saved results on the common time points within 0.01 K (largest 0.0021 K), and the nine Step 33 checks still pass.

•  Because a Step 35 check failed after SS8 was added (0.104 K against 0.1 K), the cause was traced to the solver tolerance and fixed (RelTol 1e-4); Steps 33 to 37 and the Step 34 checks were re-run on the final model.

# 11. Record of this step

| Item | Record |
| --- | --- |
| Step | 37 - Add the DGA sampling-event subsystem |
| Environment | Claude Code (this chat) through the MATLAB MCP connection (roadmap role: Simulink Agentic Toolkit; D30) |
| Completed | 13 October 2026 |
| Status | Done |
| Main inputs | Transformer_Operating_Model.slx; params_transformer.m; 03_Data/processed/dga_master.csv (columns record_id and data_role only) |
| Main outputs | Transformer_Operating_Model.slx (SS8); get_sampling_events.m; verify_step37.m; results/step37_checks.csv, step37_sampling_events.csv, step37_ss8_blocks.csv |
| Checks | verify_step37.m: 10 of 10 checks PASS (no gas block or signal; index steps at the set times; regression to the Step 36 results within 0.01 K, largest 0.0021 K) |
| Decisions | D35 (design and test of the sampling-event subsystem; two amendments), D33 amendment (solver tolerance) |

# 12. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| ST6 | IEC 60076-7:2018, Power transformers - Part 7: Loading guide for mineral-oil-immersed power transformers (Edition 2.0). The full text was NOT obtained; details TO VERIFY. Use: Basis of the top-oil and hot-spot differential equations in SS5-SS7; the thermal constants of params_transformer.m must be checked against it (TO VERIFY). |  |
| SW4 | Alliander N.V., transformer-thermal-model (IEC 60076-7 implementation, MPL-2.0), file transformer_thermal_model/transformer/power.py, class PowerTransformer, ONAF default specifications (source T1 of the Build Guide). Use: Default thermal constants of params_transformer.m (dTheta_or, g_r, H, tau_o, tau_w, k11, k21, k22, x, y) and the form of the thermal differential equations. | https://github.com/alliander-opensource/transformer-thermal-model |
| DF2 | Made in Step 9 from DS1-DS5 (Steps 5-9 programs). Use: All clean records with role, class, flags and original values. | File: 03_Data/processed/dga_master.csv; SHA-256 AE9E6C0C84CF7180... |
| DF48 | Transformer_Operating_Model.slx, built in Step 33 by build_Transformer_Operating_Model.m from the MATLAB Build Guide Part B (decisions D30, D31); MATLAB R2025b. Use: Operating-context model: load, current, oil and hot-spot temperature, ageing. Never generates gas values (D4).. | File: 05_Simulink_Model/Transformer_Operating_Model.slx; SHA-256 FB5422C605F266DF... |
| DF52 | All parameters of the transformer operating model with unit and source (E1 pandapower, T1 Alliander). Step 33 added the constant T_zero_C_in_K = 273.15 K. Use: The only place where model values are defined; read by the model callbacks. | File: 05_Simulink_Model/params_transformer.m; SHA-256 9288320B6672E1A1... |
| DF69 | step37_checks.csv (10 checks of verify_step37.m), step37_sampling_events.csv (sampling times, record_index, record_id), step37_ss8_blocks.csv (the 13 blocks of SS8). Use: Evidence that SS8 produces events only and leaves the temperatures unchanged. | File: 05_Simulink_Model/results/step37_checks.csv; SHA-256 F9D20E74ECB8E28D... |
| DF70 | verify_step37.m, get_sampling_events.m, params_transformer.m and build_Transformer_Operating_Model.m as at the end of Step 37 (solver tolerance 1e-4). Use: Fingerprints of the Step 37 code. | File: 05_Simulink_Model/code_manifest_step37.sha256; SHA-256 7F25BF7CFCCA327F... |

# 13. How this helps the next steps

Next step: Step 38 (Claude Code): build the FastAPI service in 09_API_FastAPI (stage H).

•  Step 38 (the FastAPI service) and the dashboard can call the model for an operating context and ask get_sampling_events for the record_id that belongs to each sampling event; the gases are then read from the real record in the CSV, never from the model.

•  The solver tolerance now stored in params_transformer.m makes the verification of Step 35 pass with a wide margin (0.013 K against 0.1 K).

# 14. Open items and limitations

•  The sampling times (6, 12, 18 and 22 h) are illustrative, not a real laboratory schedule; they can be replaced in params_transformer.m.

•  The held-out list is taken in file order; whether the dashboard should draw records at random or by class is a later design choice.

•  The 1 min event pulse and the order of the held-out records are choices of decision D35 (researcher may change them).

•  The regression test compares signals at the tolerance of the saved Step 36 results (RelTol 1e-3), so that only the effect of SS8 is measured; the final model runs at 1e-4 and the Step 36 results were regenerated at that tolerance.

•  Model Advisor and checklist D1 were repeated: the same 11 warnings and 1 incomplete item as accepted in D32; item D1.7 (a second team member checks the build) still needs a person.

•  The researcher's error text from the earlier Simulink rerun has still not been supplied.

# 15. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Inspection-based label | fault confirmed by opening the equipment | The fault type was seen by engineers after the unit was opened, not guessed from the gases. |
| Training (development) set | records used to build the models | 439 clean records from the Dissanayake training file. |
| Internal test set | Dissanayake unseen test file | 70 records (61 independent of the benchmark) kept away from training. |
| External test set | Li (2019) dataset | 201 records from a different source (86 independent of the benchmark), used to test the models on new data. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| FastAPI | Python web framework | Used later to make the diagnosis available as a web service (API = application programming interface). |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| Simulink, Simscape | MATLAB's block-diagram modelling tool and its physical-modelling library | Used to model the transformer's operating conditions (Simulink Agentic Toolkit); it never makes gas values. |
| D1-D35 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| Hyperparameter grid | list of settings tried for a model | For example C and gamma of the SVM; the best combination is chosen in the inner loop (Analysis Plan 5.2). |
| Tolerance (delta) | largest acceptable loss | Fixed before the study at 0.05 macro-F1 (5 percentage points), approved in Step 4. |
| Simulink | MathWorks block-diagram simulation environment | Software in which the model is drawn as blocks and lines and simulated over time. |
| Simscape | Physical modelling extension of Simulink | Blocks that follow physical laws (electrical, thermal) and connect like real components, not like signals. |
| Subsystem (SS1-SS7) | A group of blocks shown as one block | The model is split into seven subsystems: grid, transformer, measurement, load, losses to heat, thermal network, outputs and ageing. |
| Top-oil temperature | Temperature of the oil at the top of the tank | The oil temperature used in the thermal model; it rises with load and falls back towards ambient. |
| Hot-spot temperature | Temperature of the hottest part of the winding | The winding temperature that mostly decides how fast the paper insulation ages; it is the top-oil temperature plus a load-dependent rise. |
| Relative ageing rate V | How many times faster than normal the paper ages | V = 1 at the reference hot-spot temperature (98 degC); every 6 K more doubles it. The loss of life is the sum of V over time. |
| IEC 60076-7 | IEC loading guide for oil-immersed power transformers | The standard that gives the equations for oil and hot-spot temperature and for ageing under a changing load. |
| Model Advisor | MathWorks tool that checks a Simulink model against a list of rules | A built-in inspector. It runs many checks (settings, unconnected ports, style rules) and reports each as passed, warning or failed. |
| Sampling event | A moment in simulated time at which a gas sample would be taken | The model only says when; the gas values come from the real measured record in the data file, never from the model. |
| Held-out record | A record of the master table that is not used for development | A record kept aside (benchmark, internal test or external test) so that the methods are judged on data they did not learn from. |
| Solver tolerance (RelTol) | Relative accuracy that the variable-step solver keeps at each step | A smaller RelTol makes the solver take smaller steps: the result is more exact and the run slower. |