Step 39 Report

Build the App Designer dashboard

Environment: Claude Code (this chat), MATLAB through the MCP connection   |   Completed: 13 October 2026   |   Report version 2 (13 October 2026; layout and Figure 4.22 updated in Step 40)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The engineer's dashboard, DGADashboard.mlapp, was built. It loads a measured record, computes the Rogers, IEC 60599 and Duval Triangle 1 diagnoses in MATLAB, asks the FastAPI service of Step 38 for the machine-learning class and probabilities, draws the sample in the Duval Triangle, shows an agreement lamp and shows the simulated operating temperatures as context. The roadmap check was passed: three known records (one per fault family) give the same answers as the offline results, and so do all 388 held-out records (largest probability difference 0.0e+0). All 19 checks pass, including the cases where the service is not reachable or the gas values are invalid: the app shows a message and does not stop. The file was written with an internal MathWorks serializer and should be opened once in App Designer.

# 1. Purpose of this step

The dashboard is the engineer's screen of the framework (Objective 4). It must show the conventional and the machine-learning diagnoses side by side for the same measured record, and it must give the same answers as the offline results, because the thesis compares those answers.

# 2. Method used

## Approach

The dashboard is a client: it holds no diagnosis rule of its own. It reads one measured record, computes the three conventional diagnoses (Rogers ratio, IEC 60599 ratio, Duval Triangle 1) with the MATLAB functions of folder 04, and asks the FastAPI service of Step 38 for the machine-learning class and the seven class probabilities. The sample is drawn in the Duval Triangle and the answers are shown side by side, with a lamp that says whether the methods agree.

Agreement has to be defined because some conventional answers are not a single class. A conventional answer agrees with the ML class if it is equal to it; the IEC dual answer D1/D2 agrees if the ML class is D1 or D2; DT (Duval) and ND (no diagnosis) never agree. The lamp is green when all three conventional methods agree with ML, amber when at least one does not, and grey when the ML answer is not available (decision D37; the scoring rules of D11 and D25 are reused).

The service call is made with webwrite after the five gases have been checked locally. If the service cannot be reached, if a gas is missing or negative, or if the file cannot be read, the app writes a status text and keeps the conventional answers; it never stops. The simulated operating temperature (Simulink model) is shown as context only and is never linked to the measured gases.

The app file DGADashboard.mlapp is written from a component list with the internal serializer of MATLAB R2025b, because App Designer cannot be driven from code. It was read back with App Designer's own reader and run from the file.

## Why this method

•  One implementation per method: the conventional methods stay in MATLAB (folder 04) and the ML model stays in Python behind the service, so the dashboard cannot disagree with the offline results because of a second copy of the code.

•  The roadmap check is a comparison with the offline results. It is made on the three prescribed records through the real Diagnose button, and on all 388 held-out records through the same functions, so that the test is much stronger than three examples.

•  A dashboard that stops on an error would be useless in a test bench, and one that hides a failure would be misleading; therefore each failure gives a clear status text.

## Settings and rules

| Setting | Value |
| --- | --- |
| Service | http://127.0.0.1:8000/diagnose (this computer only), timeout 10 s, JSON |
| Input checks | five gases, each one finite number >= 0 (ppm); record_id and equipment_type read from the file when present |
| Three known records | first held-out, in-scope record in file order of class PD, D2 and T3 (rule of D37 fixed before running): rows 1, 36, 100 |
| Agreement lamp | green all three agree with ML; amber at least one does not; grey ML not available |
| Operating context | run_transformer_simulation, 24 h, rated load; temperatures only |
| Software | MATLAB 25.2.0.2998904 (R2025b), App Designer file format, webwrite; service: FastAPI (Step 38) |

## Equations

a=k=13Ik#1

where:

a  –  number of conventional methods that agree with ML, 0 to 3

k  –  index of the conventional method (Rogers, IEC 60599, Duval)

Ik  –  agreement indicator of method k: 1 if the answer of method k equals the ML class, or is D1/D2 and the ML class is D1 or D2; 0 otherwise (including DT and ND)

## Tools and programs

•  10_Dashboard_Client/DGADashboard.mlapp (the app); dga_agreement.m, ml_diagnose.m, load_dga_record.m

•  10_Dashboard_Client/tools/build_dashboard_mlapp.m, DGADashboard_code.txt (writes the .mlapp); tools/make_figure_4_22.m (Figure 4.22)

•  10_Dashboard_Client/verify_step39.m (19 checks)

•  00_Project_Admin/report_builder/update_register_step39.ps1 (register, glossary)

## Method references

[ST6] IEC 60076-7:2018, Power transformers - Part 7: Loading guide for mineral-oil-immersed power transformers (Edition 2.0). The full text was NOT obtained; details TO VERIFY.

[SW4] Alliander N.V., transformer-thermal-model (IEC 60076-7 implementation, MPL-2.0), file transformer_thermal_model/transformer/power.py, class PowerTransformer, ONAF default specifications (source T1 of the Build Guide). https://github.com/alliander-opensource/transformer-thermal-model

[DF2] Made in Step 9 from DS1-DS5 (Steps 5-9 programs).

# 3. What was used

•  MATLAB_Build_Guide Part C (components C2, callbacks C4) and the programmatic reference DGADashboard_reference.m.

•  The FastAPI service of Step 38 and its description 09_API_FastAPI/openapi.json (POST /diagnose).

•  The conventional functions of 04_MATLAB_Conventional, the Duval zones of 02_Standards, and the Simulink model of Steps 33 to 37 (run_transformer_simulation).

•  The offline results to compare with: 11_Results/conventional/conventional_predictions.csv and 11_Results/ml/ml_predictions.csv.

# 4. What was done, step by step

1.  Fixed the design in the decision log (D37) before building: components, agreement rule, how the three records are chosen, how failures are shown, how the .mlapp is produced, Figure 4.22.

2.  Wrote the helper functions: ml_diagnose.m (webwrite client, never stops), dga_agreement.m (agreement rule), and extended load_dga_record.m (record_id, equipment_type).

3.  Wrote the app: component list and callbacks in tools/build_dashboard_mlapp.m and tools/DGADashboard_code.txt; produced DGADashboard.mlapp with the serializer; read it back with App Designer's reader and ran it from the file.

4.  Wrote verify_step39.m (19 checks) and ran it with the service running.

5.  Produced Figure 4.22. The first screenshot showed that the results table was too short (the ML row was hidden behind a scroll bar) and that some labels covered text; the layout and the labels were corrected and the checks were run again.

6.  Wrote this report and updated the register, glossary, READMEs, CHANGELOG.md and SESSION_SUMMARY.md.

# 5. What we found

## The three known records

| Row | Record | Family | True class | Rogers / IEC / Duval | ML | Lamp |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | IECTC10_0001 | partial discharge | PD | ND/PD/PD | PD | amber |
| 36 | IECTC10_0036 | electrical discharge | D2 | D2/D1/D2/D2 | D2 | green |
| 100 | IECTC10_0100 | thermal fault | T3 | T2/T2/T3 | T2 | amber |

Each record is the first held-out, in-scope record in file order of its class (decision D37). The answers shown in the app were taken from the Diagnose button and equal the offline results; the ML probabilities differ from the offline file by at most 0.0e+0. The record of the thermal family has the true class T3, but both the conventional methods and the model give T2: the check is identity with the offline results, not correctness.

## All held-out records

The same functions that the Diagnose button calls (load_dga_record, conventional_diagnosis, ml_diagnose) were applied to all 388 held-out records: the three conventional answers, the ML class and the seven probabilities equal the offline results in every case (388 of 388). The median time of a service call was 78 ms; this is preliminary, the formal response time is measured in Step 42.

## Figure 4.22

Figure 4.22  The diagnostic dashboard after a simulation run and the diagnosis of record IECTC10_0001 (annotated)

| No. | Component | What it shows |
| --- | --- | --- |
| 1 | RunSimulationButton | Run transformer simulation: plots the operating temperatures (context only) |
| 2 | LoadDGAFileButton | Load measured DGA file; the record number is chosen with the spinner below it |
| 3 | DiagnoseButton | Diagnose selected record: conventional methods in MATLAB, ML through the service |
| 4 | GasTable | The five measured gases of the record (ppm), unchanged from the file |
| 5 | UIAxesTemperature | Operating condition: top-oil and hot-spot temperature from the Simulink model |
| 6 | UIAxesDuval | Duval Triangle 1 with the measured sample |
| 7 | ResultsTable | Rogers, IEC 60599, Duval and ML diagnoses, and whether each agrees with ML |
| 8 | ProbabilityTable | ML class probabilities from the service |
| 9 | EventTable | Sampling events of the simulated day (dotted lines in 5): record, ML class, agreement, hot-spot temperature |
| 10 | ModelLabel | Model name, version, hash, confidence and response time |
| 11 | AgreementLabel | Agreement flag: green all agree, amber disagree, grey ML not available |

# 6. Checks

| Check (verify_step39.m) | Result |
| --- | --- |
| DGADashboard.mlapp loads with App Designer's reader; the 13 components of Build Guide C2, 3 callbacks and startupFcn are present | PASS |
| the app starts from the file: startup text, grey lamp, service address set | PASS |
| the offline conventional file has the methods IEC60599, Rogers, Duval | PASS |
| record 1 (IECTC10_0001, partial discharge): conventional answers equal the offline results | PASS |
| record 1 (IECTC10_0001): ML class and 7 probabilities equal the offline results | PASS |
| record 1 (IECTC10_0001): agreement flag, gas table, probability table and Duval plot as expected | PASS |
| record 36 (IECTC10_0036, electrical discharge): conventional answers equal the offline results | PASS |
| record 36 (IECTC10_0036): ML class and 7 probabilities equal the offline results | PASS |
| record 36 (IECTC10_0036): agreement flag, gas table, probability table and Duval plot as expected | PASS |
| record 100 (IECTC10_0100, thermal fault): conventional answers equal the offline results | PASS |
| record 100 (IECTC10_0100): ML class and 7 probabilities equal the offline results | PASS |
| record 100 (IECTC10_0100): agreement flag, gas table, probability table and Duval plot as expected | PASS |
| all 388 held-out records: three conventional answers and the ML class and probabilities equal the offline results | PASS |
| service not reachable: status NOT_CONNECTED, grey lamp, conventional answers still shown, no error | PASS |
| invalid gas values (negative H2, missing CH4): INVALID_INPUT, grey lamp, no error | PASS |
| file without gas columns: a message in the status line, no error | PASS |
| Diagnose pressed before a file is loaded: a message, no error | PASS |
| agreement rule: equal agrees; D1/D2 agrees with D1 or D2; DT and ND never agree; no ML result gives grey | PASS |
| Run transformer simulation: temperature plot (top-oil, hot-spot) and status with final hot-spot 100.3 degC (24 h rated load) | PASS |

# 7. Problems and fixes

•  App Designer cannot be driven from code, so the .mlapp was written with an internal serializer. A first file lost the component names because the helper used by MATLAB at run time marks them as transient; the names are now added as App Designer adds them, and the file was read back to show that all 20 components keep their names, code and callbacks.

•  The first screenshot of the app showed only two of the four rows of the results table (the ML row was hidden) and numbered labels that covered text. The row heights of the layout were changed and the labels moved; the checks were run again on the final file.

•  In Step 40 the layout was made compact (the window is cut to about 750 pixels in height on this computer) and an event table was added; Figure 4.22 and its legend were made again, and the agreement text was shortened to fit. The 19 checks of this step were run again on the final file and pass.

•  A first version of the test compared an empty text string with isempty, which is false for strings; the test now sets the property empty.

# 8. Decisions

•  D37: the components, the agreement rule (D1/D2 agrees with D1 or D2; DT and ND never agree), the rule for the three records, the status texts for failures, the production of the .mlapp, and Figure 4.22.

# 9. Files produced

•  10_Dashboard_Client/DGADashboard.mlapp, dga_agreement.m, ml_diagnose.m, load_dga_record.m, verify_step39.m, tools/build_dashboard_mlapp.m, tools/DGADashboard_code.txt, tools/make_figure_4_22.m, code_manifest_step39.sha256

•  10_Dashboard_Client/results/step39_checks.csv, step39_three_records.csv, step39_held_out_comparison.csv

•  11_Results/figures/F4_22_dashboard_annotated.png, .pdf, F4_22_dashboard_annotated_legend.csv, F4_22_dashboard_raw.png

# 10. What was achieved

•  The App Designer dashboard DGADashboard.mlapp was built: it loads a record, shows the three conventional diagnoses computed in MATLAB, calls the service for the ML diagnosis and class probabilities, draws the sample in Duval Triangle 1, shows the agreement lamp and the simulated operating temperatures (decision D37).

•  All 19 checks pass. The three known records (one per fault family) give exactly the offline conventional answers, the offline ML class and the offline probabilities (largest difference 0.0e+0); the same holds for all 388 held-out records.

•  Service not reachable, invalid gas values, an unreadable file and a missing file each give a status text and no error.

•  Figure 4.22 (annotated screenshot) was produced.

# 11. Record of this step

| Item | Record |
| --- | --- |
| Step | 39 - Build the App Designer dashboard |
| Environment | Claude Code (this chat) through the MATLAB MCP connection (roadmap role: MATLAB Agentic Toolkit; D30) |
| Completed | 13 October 2026 |
| Status | Done (the .mlapp should be opened once in App Designer by the researcher) |
| Main inputs | MATLAB_Build_Guide Part C; 09_API_FastAPI/openapi.json and the running service; dga_master.csv; the offline results of Steps 14 and 22 |
| Main outputs | 10_Dashboard_Client/DGADashboard.mlapp, dga_agreement.m, ml_diagnose.m, load_dga_record.m, verify_step39.m, results/step39_*.csv; 11_Results/figures/F4_22_dashboard_annotated.(png¦pdf), legend csv |
| Checks | verify_step39.m: 19 of 19 checks PASS; 3 known records and all 388 held-out records equal the offline results (largest probability difference 0.0e+0) |
| Decisions | D37 (dashboard design, agreement rule, record rule, .mlapp production) |

# 12. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| ST6 | IEC 60076-7:2018, Power transformers - Part 7: Loading guide for mineral-oil-immersed power transformers (Edition 2.0). The full text was NOT obtained; details TO VERIFY. Use: Basis of the top-oil and hot-spot differential equations in SS5-SS7; the thermal constants of params_transformer.m must be checked against it (TO VERIFY). |  |
| SW4 | Alliander N.V., transformer-thermal-model (IEC 60076-7 implementation, MPL-2.0), file transformer_thermal_model/transformer/power.py, class PowerTransformer, ONAF default specifications (source T1 of the Build Guide). Use: Default thermal constants of params_transformer.m (dTheta_or, g_r, H, tau_o, tau_w, k11, k21, k22, x, y) and the form of the thermal differential equations. | https://github.com/alliander-opensource/transformer-thermal-model |
| DF2 | Made in Step 9 from DS1-DS5 (Steps 5-9 programs). Use: All clean records with role, class, flags and original values. | File: 03_Data/processed/dga_master.csv; SHA-256 AE9E6C0C84CF7180... |
| DF48 | Transformer_Operating_Model.slx, built in Step 33 by build_Transformer_Operating_Model.m from the MATLAB Build Guide Part B (decisions D30, D31); MATLAB R2025b. Use: Operating-context model: load, current, oil and hot-spot temperature, ageing. Never generates gas values (D4).. | File: 05_Simulink_Model/Transformer_Operating_Model.slx; SHA-256 FB5422C605F266DF... |
| DF52 | All parameters of the transformer operating model with unit and source (E1 pandapower, T1 Alliander). Step 33 added the constant T_zero_C_in_K = 273.15 K. Use: The only place where model values are defined; read by the model callbacks. | File: 05_Simulink_Model/params_transformer.m; SHA-256 9288320B6672E1A1... |
| DF71 | step39_checks.csv (19 checks of verify_step39.m), step39_three_records.csv (the three known records), step39_held_out_comparison.csv (388 held-out records: app answers against offline results). Use: Evidence for the Step 39 check: known records give the offline answers. | File: 10_Dashboard_Client/results/step39_checks.csv; SHA-256 2DA3E3899E47A1C5... |
| DF72 | Screenshot of DGADashboard after a simulation run and the diagnosis of record IECTC10_0001 (exportapp), with numbered labels; .pdf and legend .csv beside it. Use: Figure 4.22 of the thesis. | File: 11_Results/figures/F4_22_dashboard_annotated.png; SHA-256 9B5BED113892E441... |
| DF73 | DGADashboard.mlapp, dga_agreement.m, ml_diagnose.m, load_dga_record.m, verify_step39.m, tools/build_dashboard_mlapp.m, tools/DGADashboard_code.txt, tools/make_figure_4_22.m. Use: Fingerprints of the Step 39 code. | File: 10_Dashboard_Client/code_manifest_step39.sha256; SHA-256 23927D8B58E3E01E... |

# 13. How this helps the next steps

Next step: Step 40 (Simulink Agentic Toolkit): let the dashboard run the Simulink model with a Run Simulation button and use the sampling events of SS8 to trigger the diagnosis of the next record.

•  Step 40 adds the Run Simulation link and uses the sampling events of SS8 to trigger the diagnosis of the next record: the dashboard already diagnoses any row of dga_master.csv, and get_sampling_events.m gives the row from record_index.

•  Steps 41 and 42 (test bench, fidelity and response time) can call the same helper functions; the comparison of this step already shows 100 % identity with the offline results.

•  Chapter 4 can show Figure 4.22 and the table of the three records (results/step39_three_records.csv).

# 14. Open items and limitations

•  DGADashboard.mlapp was written with an internal MathWorks serializer, not drawn in App Designer. It loads with App Designer's reader and runs, but it should be opened once in App Designer and saved there (decision D37, clause 7).

•  The agreement definition (D1/D2 agrees with D1 or D2; DT and ND never agree) and the choice of the three records are choices of decision D37; the researcher may change them.

•  The three known records are the first of their class in file order; the ML class of the thermal record (T2) differs from its true class T3. The check is identity with the offline results, not correctness.

•  The service must be started before the app (09_API_FastAPI/run_service.ps1); otherwise the ML row shows NOT_CONNECTED and the lamp is grey.

•  The response times in the app (about 75 to 100 ms per call) are preliminary; the formal response time is measured in Step 42.

•  The researcher's error text from the earlier Simulink rerun has still not been supplied.

# 15. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| D2 | discharges of high energy | Arcing with power follow-through: extensive carbonisation, metal fusion, sometimes tripping of the equipment. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| T2 | thermal fault 300 to 700 °C | Overheating in which the paper has carbonised. |
| T3 | thermal fault above 700 °C | Very hot fault: carbonised oil, metal colouring (800 °C) or metal fusion (above 1 000 °C). |
| DT | mixture of thermal and electrical faults | A zone of the Duval Triangle 1 for cases that look partly thermal and partly electrical. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| Duval Triangle 1 | graphical DGA method by M. Duval | The shares of CH4, C2H4 and C2H2 are plotted as one point in a triangle divided into fault zones. |
| Rogers ratios | older gas-ratio method by R.R. Rogers | A ratio table that names faults from three gas ratios; kept in IEEE C57.104. |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Not detected | gas below the laboratory's detection limit | Treated as 0 ppm in this thesis (decision D8). |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Median, quartiles | middle value and the values a quarter and three quarters of the way up | Describe typical gas levels without being pulled by extreme values. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| Simulink, Simscape | MATLAB's block-diagram modelling tool and its physical-modelling library | Used to model the transformer's operating conditions (Simulink Agentic Toolkit); it never makes gas values. |
| D1-D38 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| ND (no diagnosis) | No diagnosis | The answer of a method when no rule applies or a ratio it needs cannot be calculated. It is a result and is never deleted. |
| Dual answer (D1/D2) | Two classes returned together | Sometimes the IEC table fits two fault types at once. The method then answers with both (D1/D2); it counts as correct if the true class is either one. |
| Class probability | model's confidence in each class | For every record the model gives a probability for each of the seven classes; they add up to 1 and the largest is the prediction. |
| Simulink | MathWorks block-diagram simulation environment | Software in which the model is drawn as blocks and lines and simulated over time. |
| Subsystem (SS1-SS7) | A group of blocks shown as one block | The model is split into seven subsystems: grid, transformer, measurement, load, losses to heat, thermal network, outputs and ageing. |
| Top-oil temperature | Temperature of the oil at the top of the tank | The oil temperature used in the thermal model; it rises with load and falls back towards ambient. |
| Hot-spot temperature | Temperature of the hottest part of the winding | The winding temperature that mostly decides how fast the paper insulation ages; it is the top-oil temperature plus a load-dependent rise. |
| Relative ageing rate V | How many times faster than normal the paper ages | V = 1 at the reference hot-spot temperature (98 degC); every 6 K more doubles it. The loss of life is the sum of V over time. |
| IEC 60076-7 | IEC loading guide for oil-immersed power transformers | The standard that gives the equations for oil and hot-spot temperature and for ageing under a changing load. |
| Sampling event | A moment in simulated time at which a gas sample would be taken | The model only says when; the gas values come from the real measured record in the data file, never from the model. |
| Held-out record | A record of the master table that is not used for development | A record kept aside (benchmark, internal test or external test) so that the methods are judged on data they did not learn from. |
| JSON | JavaScript Object Notation | A plain-text format for named values, e.g. {"H2": 200}; requests and answers of the service are written in it. |
| OpenAPI (openapi.json) | standard description of a web interface | A file that lists every address of the service, what it must be sent and what it answers, so another program can be built against it. |
| FastAPI | Python framework for web services | The library used to build the diagnosis service; it also checks every input against the declared rules. |
| Endpoint | one address of a web service | For example POST /diagnose (send a sample, get a diagnosis) or GET /health (is the service alive?). |
| 127.0.0.1 (localhost) | the address of the computer itself | A service on 127.0.0.1 can be reached only from the same computer, not from the network. |
| Fidelity | share of records for which the service gives exactly the offline answer | F = matches / records sent (Analysis Plan Eq. 47); the requirement is 100 %. |
| Agreement flag | Lamp that says whether the conventional methods agree with the ML diagnosis | Green: all three conventional methods give the same class as ML. Amber: at least one does not. Grey: no ML answer. |
| webwrite | MATLAB function that sends data to a web service | How the dashboard sends the five gas values to the FastAPI service and receives the ML class. |
| App Designer | MATLAB tool for building apps (.mlapp files) | The program in which DGADashboard.mlapp is edited; the file can also be run without opening it. |
| Event table | List of the sampling events of a simulated run in the dashboard | One row per sampling event: time, record, ML class, how many conventional methods agree, and the simulated hot-spot temperature at that time. |