Step 40 Report

Link the Simulink model to the dashboard

Environment: Claude Code (this chat), MATLAB and Simulink through the MCP connection   |   Completed: 13 October 2026   |   Report version 1 (13 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The Run Simulation button of the dashboard now runs the Simulink transformer model for a full simulated day (24 hours, 1.1 s) and plays back the 4 sampling events of subsystem SS8 at 6, 12, 18, 22 hours: at each event the dashboard looks up the record with the given record_id in the DGA file, diagnoses it with the three conventional methods and the ML service, and lists it in an event table together with the simulated hot-spot temperature of that moment. The model was not changed. All 13 checks pass: the events equal those of Step 37, every diagnosis equals the offline result, no gas value comes from the model, and the run also completes without the service, without a loaded file, and with a file that lacks some of the records. The 19 checks of Step 39 still pass.

# 1. Purpose of this step

This step turns the dashboard and the model into one test bench: the simulated transformer decides when a sample is taken (the sampling events), and the dashboard diagnoses the measured record that belongs to that moment. The check of the roadmap is that a full simulated day runs from the app without error.

# 2. Method used

## Approach

The Run Simulation button of the dashboard now runs the Simulink operating model (sim of Transformer_Operating_Model, through run_transformer_simulation) for a full simulated day of 24 hours. The model itself is not changed: its subsystem SS8 (Step 37) already counts the sampling times and logs record_index. After the run, the function get_sampling_events turns the logged index into a table of sampling events (time, index, record_id), outside the model.

The dashboard then plays the events back in time order. For each event it finds the row of that record_id in the loaded DGA file, selects it, and diagnoses it with the same code as the Diagnose button: the three conventional diagnoses in MATLAB and the ML diagnosis from the service. The events are marked on the temperature plot and listed in a table with the simulated hot-spot temperature at that moment. That temperature is operating context shown next to the record; it is not used to diagnose it.

The link carries a record identifier only. The model never holds or produces a gas value: the gases are read from the file row of the record, as in Step 39. If no file is loaded the app uses dga_master.csv and says so; a record that is not in the file is reported and skipped; if the service is not reachable the run still completes and each event shows NOT_CONNECTED (decision D38).

## Why this method

•  The roadmap asks for a working test bench in which the simulated transformer decides when a sample is taken and the dashboard diagnoses the sample of that moment. Passing only the record identifier keeps the rule of decision D4 (no gas value is generated by the model) true by construction.

•  A single diagnosis function for the button and for the events means that Step 39's comparison with the offline results also covers the events; it is repeated here for the event records.

•  Playing the events back after the run (instead of during it) keeps the simulation itself unchanged and repeatable.

## Settings and rules

| Setting | Value |
| --- | --- |
| Run | 24 h, default load profile of params_transformer.m (rated load), solver RelTol 1e-4 (D33) |
| Sampling events | at 6, 12, 18, 22 h (illustrative, D35); 4 events |
| Playback | events in time order; pause 0.5 s between events (0 s in the tests) |
| Records | the first held-out records of dga_master.csv, looked up by record_id in the loaded file |
| Service | http://127.0.0.1:8000/diagnose, as in Step 39 |
| Software | MATLAB 25.2.0.2998904 (R2025b), Simulink, Simscape; service: FastAPI (Step 38) |

## Tools and programs

•  10_Dashboard_Client/DGADashboard.mlapp (Run Simulation button, EventTable); find_dga_row.m

•  05_Simulink_Model/run_transformer_simulation.m (returns res.events), get_sampling_events.m

•  10_Dashboard_Client/verify_step40.m (13 checks)

•  00_Project_Admin/report_builder/update_register_step40.ps1 (register, glossary)

## Method references

[ST6] IEC 60076-7:2018, Power transformers - Part 7: Loading guide for mineral-oil-immersed power transformers (Edition 2.0). The full text was NOT obtained; details TO VERIFY.

[SW4] Alliander N.V., transformer-thermal-model (IEC 60076-7 implementation, MPL-2.0), file transformer_thermal_model/transformer/power.py, class PowerTransformer, ONAF default specifications (source T1 of the Build Guide). https://github.com/alliander-opensource/transformer-thermal-model

[DF2] Made in Step 9 from DS1-DS5 (Steps 5-9 programs).

# 3. What was used

•  Transformer_Operating_Model.slx with the sampling-event subsystem SS8 (Step 37), unchanged.

•  DGADashboard.mlapp and its helper functions (Step 39); the FastAPI service (Step 38).

•  get_sampling_events.m (look-up of the record_id from the logged index) and the held-out list of params_transformer.m.

# 4. What was done, step by step

1.  Fixed the design in the decision log (D38) before changing anything: the model stays unchanged, what the dashboard does with the events, what happens without a file, and the checks.

2.  Extended run_transformer_simulation.m to return the sampling events, and wrote find_dga_row.m (row of a record_id in the file; reads only that column).

3.  Changed the dashboard: the diagnosis was moved into one function used by the Diagnose button and by the events; the Run Simulation callback marks the events on the plot and plays them back; a new event table lists them. The .mlapp was written again.

4.  Wrote verify_step40.m (13 checks, including the 19 checks of Step 39) and ran it with the service running.

5.  Produced the event listing of the full day (results/step40_event_run.csv) and regenerated Figure 4.22 so that it shows the final app.

6.  Wrote this report and updated the register, glossary, READMEs, CHANGELOG.md and SESSION_SUMMARY.md.

# 5. What we found

## The simulated day

| Event | Time (h) | Record | ML class | Conventional methods agreeing (of 3) | Simulated hot-spot (degC) |
| --- | --- | --- | --- | --- | --- |
| 1 | 6.0 | IECTC10_0001 | PD | 2 | 99.97 |
| 2 | 12.0 | IECTC10_0002 | PD | 2 | 100.27 |
| 3 | 18.0 | IECTC10_0003 | PD | 1 | 100.28 |
| 4 | 22.0 | IECTC10_0004 | PD | 1 | 100.28 |

The record identifiers are those of the first four held-out records (Step 37). The hot-spot temperature is the simulated operating condition at the time of the event; it is displayed beside the record and has no part in its diagnosis. At 6 hours the hot spot is still rising, later it is close to its final value of about 100.3 degC.

## Figure 4.22 (regenerated)

Figure 4.22  The diagnostic dashboard after a simulated day and the diagnosis of record IECTC10_0001 (annotated)

The temperature plot shows the numbered sampling events as dotted lines; the event table at the right lists the four records diagnosed during the run.

# 6. Checks

| Check (verify_step40.m) | Result |
| --- | --- |
| a full simulated day (24 h) runs from the Run Simulation button without error and is plotted | PASS |
| no DGA file loaded: the app uses dga_master.csv and says so | PASS |
| the sampling events passed to the dashboard equal those of Step 37 (times, indices, record_ids); the table holds no gas value | PASS |
| every sampling event is marked on the temperature plot at its time | PASS |
| at each sampling event the next record is diagnosed in time order; conventional answers, ML class and probabilities equal the offline results | PASS |
| the gas values used at the events are those of the file rows (nothing comes from the model) | PASS |
| event table: time, record, ML class and the simulated hot-spot temperature at that time | PASS |
| the temperatures plotted by the app equal run_transformer_simulation of the unchanged model | PASS |
| the same run twice gives the same events and replaces the table (4 rows, not 8) | PASS |
| service not reachable during the run: the day still runs, every event shows NOT_CONNECTED, no error | PASS |
| records of other events missing from the loaded file are skipped with a message, no error | PASS |
| the model file is unchanged by the app runs (checksum) | PASS |
| the 19 checks of verify_step39.m still pass with the new app | PASS |

# 7. Problems and fixes

•  The tests found a fault in the app: the dotted event lines are hidden from the legend, and a hidden object is not removed when the plot is redrawn, so a second run showed eight lines instead of four. The old lines are now deleted before each plot; the test of the repeated run passes.

•  The first test run also failed on the event markers because the test searched with a function that does not see hidden objects; the test was corrected, not the app.

•  The first screenshot with the event table showed that the window is cut to about 750 pixels in height on this computer: the temperature plot was squeezed and the table was cut off. The layout was redesigned (event table in the bottom row, model label and agreement flag at the bottom right) and the screenshot, which first showed record 4 instead of the chosen record, was corrected and made again. Figure 4.22 of Step 39 no longer matched the app, so the report of Step 39 was rebuilt as version 2.

# 8. Decisions

•  D38: the model unchanged; events returned by run_transformer_simulation; playback and one diagnosis function; default file; checks.

# 9. Files produced

•  10_Dashboard_Client/DGADashboard.mlapp (updated), find_dga_row.m, verify_step40.m, tools/build_dashboard_mlapp.m, tools/DGADashboard_code.txt, code_manifest_step40.sha256

•  05_Simulink_Model/run_transformer_simulation.m (updated)

•  10_Dashboard_Client/results/step40_checks.csv, step40_event_run.csv

•  11_Results/figures/F4_22_dashboard_annotated.png (regenerated)

# 10. What was achieved

•  The Run Simulation button now runs the model for a full simulated day, marks the sampling events on the temperature plot, and diagnoses the record of each event in time order (decision D38).

•  All 13 checks pass: the day runs without error (1.1 s), the 4 events equal those of Step 37, and the diagnosis at each event equals the offline conventional and ML results.

•  The model file is unchanged (checksum), the plotted temperatures equal those of run_transformer_simulation, and no gas value comes from the model.

•  Without the service, without a loaded file, and with a file that lacks some of the records, the run completes with a clear message.

•  The 19 checks of Step 39 still pass with the new app.

# 11. Record of this step

| Item | Record |
| --- | --- |
| Step | 40 - Link the Simulink model to the dashboard |
| Environment | Claude Code (this chat) through the MATLAB MCP connection (roadmap role: Simulink Agentic Toolkit; D30) |
| Completed | 13 October 2026 |
| Status | Done |
| Main inputs | Transformer_Operating_Model.slx with SS8; DGADashboard.mlapp of Step 39; the service of Step 38 |
| Main outputs | DGADashboard.mlapp (updated), run_transformer_simulation.m (events), find_dga_row.m, verify_step40.m, results/step40_checks.csv, step40_event_run.csv; Figure 4.22 regenerated |
| Checks | verify_step40.m: 13 of 13 checks PASS; full 24 h day from the app in 1.1 s; 4 sampling events diagnosed, equal to the offline results; Step 39 checks (19) still pass |
| Decisions | D38 (the link, the playback, the event table, the checks) |

# 12. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| ST6 | IEC 60076-7:2018, Power transformers - Part 7: Loading guide for mineral-oil-immersed power transformers (Edition 2.0). The full text was NOT obtained; details TO VERIFY. Use: Basis of the top-oil and hot-spot differential equations in SS5-SS7; the thermal constants of params_transformer.m must be checked against it (TO VERIFY). |  |
| SW4 | Alliander N.V., transformer-thermal-model (IEC 60076-7 implementation, MPL-2.0), file transformer_thermal_model/transformer/power.py, class PowerTransformer, ONAF default specifications (source T1 of the Build Guide). Use: Default thermal constants of params_transformer.m (dTheta_or, g_r, H, tau_o, tau_w, k11, k21, k22, x, y) and the form of the thermal differential equations. | https://github.com/alliander-opensource/transformer-thermal-model |
| DF2 | Made in Step 9 from DS1-DS5 (Steps 5-9 programs). Use: All clean records with role, class, flags and original values. | File: 03_Data/processed/dga_master.csv; SHA-256 AE9E6C0C84CF7180... |
| DF48 | Transformer_Operating_Model.slx, built in Step 33 by build_Transformer_Operating_Model.m from the MATLAB Build Guide Part B (decisions D30, D31); MATLAB R2025b. Use: Operating-context model: load, current, oil and hot-spot temperature, ageing. Never generates gas values (D4).. | File: 05_Simulink_Model/Transformer_Operating_Model.slx; SHA-256 FB5422C605F266DF... |
| DF52 | All parameters of the transformer operating model with unit and source (E1 pandapower, T1 Alliander). Step 33 added the constant T_zero_C_in_K = 273.15 K. Use: The only place where model values are defined; read by the model callbacks. | File: 05_Simulink_Model/params_transformer.m; SHA-256 9288320B6672E1A1... |
| DF74 | step40_checks.csv (13 checks of verify_step40.m) and step40_event_run.csv (the four sampling events of the full simulated day as the dashboard shows them: time, record_id, ML class, conventional methods agreeing, simulated hot-spot temperature). Use: Evidence for the Step 40 check: a full simulated day runs from the app. | File: 10_Dashboard_Client/results/step40_checks.csv; SHA-256 9CA8E7417EB4A616... |
| DF75 | DGADashboard.mlapp (with the event link), find_dga_row.m, verify_step40.m, tools/build_dashboard_mlapp.m, tools/DGADashboard_code.txt, 05_Simulink_Model/run_transformer_simulation.m. Use: Fingerprints of the Step 40 code. | File: 10_Dashboard_Client/code_manifest_step40.sha256; SHA-256 E6408EE7B542CD74... |

# 13. How this helps the next steps

Next step: Step 41 (MATLAB Agentic Toolkit): run the integrated system over every held-out record of role internal test or benchmark and log each diagnosis and its response time in 10_Dashboard_Client/logs/testbench_log.csv (Figure 4.20).

•  Step 41 runs the integrated system over every held-out record and logs each diagnosis and its response time: it can use the same helper functions and the same service call; the events of this step show the path that a simulated sample takes.

•  Step 42 compares that log with the offline predictions; this step already shows identity for the event records.

# 14. Open items and limitations

•  The model was not changed in this step. The sampling times (6, 12, 18 and 22 h) are illustrative (D35).

•  The playback pause (0.5 s) and the content of the event table are choices of decision D38.

•  The events are played back after the simulation has finished, not while it runs; the simulation takes about a second, so no difference is visible to the user.

•  DGADashboard.mlapp is still a file written with an internal serializer and should be opened once in App Designer (Step 39).

•  The service must be started before the run, otherwise the ML column shows NOT_CONNECTED for every event.

•  The researcher's error text from the earlier Simulink rerun has still not been supplied.

# 15. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Internal test set | Dissanayake unseen test file | 70 records (61 independent of the benchmark) kept away from training. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| docx | Microsoft Word document | The format of these reports. |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| Simulink, Simscape | MATLAB's block-diagram modelling tool and its physical-modelling library | Used to model the transformer's operating conditions (Simulink Agentic Toolkit); it never makes gas values. |
| D1-D38 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| Simulink | MathWorks block-diagram simulation environment | Software in which the model is drawn as blocks and lines and simulated over time. |
| Simscape | Physical modelling extension of Simulink | Blocks that follow physical laws (electrical, thermal) and connect like real components, not like signals. |
| Subsystem (SS1-SS7) | A group of blocks shown as one block | The model is split into seven subsystems: grid, transformer, measurement, load, losses to heat, thermal network, outputs and ageing. |
| Top-oil temperature | Temperature of the oil at the top of the tank | The oil temperature used in the thermal model; it rises with load and falls back towards ambient. |
| Hot-spot temperature | Temperature of the hottest part of the winding | The winding temperature that mostly decides how fast the paper insulation ages; it is the top-oil temperature plus a load-dependent rise. |
| Relative ageing rate V | How many times faster than normal the paper ages | V = 1 at the reference hot-spot temperature (98 degC); every 6 K more doubles it. The loss of life is the sum of V over time. |
| IEC 60076-7 | IEC loading guide for oil-immersed power transformers | The standard that gives the equations for oil and hot-spot temperature and for ageing under a changing load. |
| Sampling event | A moment in simulated time at which a gas sample would be taken | The model only says when; the gas values come from the real measured record in the data file, never from the model. |
| Held-out record | A record of the master table that is not used for development | A record kept aside (benchmark, internal test or external test) so that the methods are judged on data they did not learn from. |
| Solver tolerance (RelTol) | Relative accuracy that the variable-step solver keeps at each step | A smaller RelTol makes the solver take smaller steps: the result is more exact and the run slower. |
| FastAPI | Python framework for web services | The library used to build the diagnosis service; it also checks every input against the declared rules. |
| Endpoint | one address of a web service | For example POST /diagnose (send a sample, get a diagnosis) or GET /health (is the service alive?). |
| 127.0.0.1 (localhost) | the address of the computer itself | A service on 127.0.0.1 can be reached only from the same computer, not from the network. |
| Agreement flag | Lamp that says whether the conventional methods agree with the ML diagnosis | Green: all three conventional methods give the same class as ML. Amber: at least one does not. Grey: no ML answer. |
| App Designer | MATLAB tool for building apps (.mlapp files) | The program in which DGADashboard.mlapp is edited; the file can also be run without opening it. |
| Event table | List of the sampling events of a simulated run in the dashboard | One row per sampling event: time, record, ML class, how many conventional methods agree, and the simulated hot-spot temperature at that time. |
| Playback | Showing the sampling events of a finished run one after the other | The dashboard steps through the events in time order and diagnoses the record of each. |