Step 42 Report

Evaluate fidelity and response time (integration report)

Environment: Claude Code (this chat)   |   Completed: 13 October 2026   |   Report version 1 (13 October 2026)

Thesis: Intelligent Power Transformer Fault Diagnosis Using Dissolved Gas Analysis and Machine Learning (MPhil, UMaT)

Abbreviations (such as PD, D1, T1, ppm) and technical terms are explained in the last section of this report.

In short: The integrated system - Simulink model, MATLAB dashboard functions and Python service - gave exactly the offline answers for all 388 held-out records: the same ML class, the same seven probabilities and the same Rogers, IEC 60599 and Duval diagnoses. Fidelity is therefore 100 %, as required, with no failed call and no mismatch to trace. The service answered in 78.6 ms (median) and 95.4 ms (95th percentile), far below the 1 s target. Table 4.11 and Figure 4.21 are made, and Stage H is complete.

# 1. Purpose of this step

This step answers the integration question of the thesis: does the integrated framework give the same answers as the offline analysis, and is it fast enough for interactive use? The Analysis Plan (Section 10) requires 100 % fidelity and proposes a 95th-percentile response time below 1 s (approved item 15). This report is also the integration report named in the roadmap.

# 2. Method used

## Approach

The log of the end-to-end test bench (Step 41) holds, for each of the 388 held-out records, what the integrated system answered - the three conventional diagnoses computed in MATLAB, the ML class and its seven probabilities returned by the Python service - and how long the service request took. Each logged answer was compared, record by record, with the answer saved by the offline analysis (ml_predictions.csv of Step 22 and conventional_predictions.csv of Step 16).

Fidelity is the share of records for which the integrated system gives exactly the offline ML class (Analysis Plan Eq. 47); a failed call or a missing record counts as a mismatch. The probabilities and the conventional answers were compared in the same way. The response time - the time between sending a request and receiving the answer - was summarised by its median and 95th percentile and judged against the approved target of 1 s.

## Why this method

•  An integrated tool is only trustworthy if it reproduces the analysis it is built on: the thesis's accuracy results apply to the dashboard only when its answers are identical, record by record, to the offline answers.

•  The 95th percentile describes the slow end that a user would notice, which the mean or median alone would hide. All records, including the first five warm-up calls, are counted in the main figure, because the plan says 'over all test records' and this is the cautious choice.

## Settings and rules

| Setting | Value |
| --- | --- |
| Records | all 388 held-out records (benchmark 117, internal test 70, external test 201), as run in Step 41 (D39) |
| Offline answers | ML: ml_predictions.csv (class and 7 probabilities); conventional: column result (after the upper normality gate, as shown by the dashboard) |
| Match rule | exact equality of the class, of each parsed probability and of each conventional answer; a failed call or missing record is a mismatch |
| Response time | response_ms of the log (tic/toc around webwrite in MATLAB); main: all 388 calls; sensitivity: without the 5 warm-up calls |
| Percentile rule | numpy.percentile with linear interpolation (as in Step 38) |
| Requirements | F = 1 (100 %); 95th percentile < 1000 ms (Analysis Plan item 15) |
| True labels | not read |

## Equations

F=nmatchN#1

where:

F  –  fidelity of the integrated system (fraction; required value 1)

nmatch  –  held-out records for which the logged ML class equals the offline class

N  –  held-out records sent to the integrated system (388)

tp95=Q0.95t1,…,tN#2

where:

tp95  –  95th percentile of the response times [ms]

ti  –  response time of request i [ms]

Q0.95  –  the 0.95 quantile with linear interpolation between ordered values

## Tools and programs

•  06_Python_ML/src/analysis/step42_integration.py (comparison, Table 4.11, Figure 4.21, integration files); tests/test_integration.py; make_chapter4.py (now also rebuilds Table 4.11 and Figure 4.21)

# 3. What was done, step by step

1.  Read the Step 41 outputs (log, run information, checks) and confirmed that Steps 39-41 had been completed in the parallel MATLAB session.

2.  Fixed the evaluation rules before computing anything (decision D40).

3.  Wrote step42_integration.py: join the log with the offline files, compare every answer, compute fidelity and time statistics, write Table 4.11, Figure 4.21 and the integration files.

4.  Added the program to make_chapter4.py, protected the MATLAB-made tables and figures there, and ran the rebuild check.

5.  Wrote three tests (test_integration.py) and ran the whole suite (154 tests).

# 4. Results

## Table 4.11  Integration fidelity and response time

| Measure | Records | Value | Requirement - met |
| --- | --- | --- | --- |
| ML class identical to the offline prediction (F, Eq. 47) | 388/388 | 100.0 % | F = 1 - yes |
| ML class identical - IEC TC 10 benchmark | 117/117 | 100.0 % | F = 1 - yes |
| ML class identical - internal test | 70/70 | 100.0 % | F = 1 - yes |
| ML class identical - external test (Li 2019) | 201/201 | 100.0 % | F = 1 - yes |
| All 7 class probabilities identical | 388/388 | 100.0 % |  |
| Rogers Ratio answer identical to the offline result | 388/388 | 100.0 % |  |
| IEC 60599 ratio answer identical to the offline result | 388/388 | 100.0 % |  |
| Duval Triangle 1 answer identical to the offline result | 388/388 | 100.0 % |  |
| Failed service calls | 0/388 | 0 | 0 - yes |
| Service request: median - all records | 388 | 78.6 ms |  |
| Service request: 95th percentile - all records | 388 | 95.4 ms | < 1000 ms - yes |
| Service request: median - without the 5 warm-up calls | 383 | 78.5 ms |  |
| Service request: 95th percentile - without the 5 warm-up calls | 383 | 95.1 ms |  |
| Service request: minimum - all records | 388 | 62.1 ms |  |
| Service request: maximum - all records | 388 | 157.7 ms |  |
| Conventional diagnoses (MATLAB): median - all records | 388 | 277.5 ms |  |
| Conventional diagnoses (MATLAB): 95th percentile - all records | 388 | 331.8 ms |  |
| Total per record: median - all records | 388 | 468.7 ms |  |
| Total per record: 95th percentile - all records | 388 | 548.4 ms |  |

Fidelity rows first, then the times: the service request (judged against the target), the conventional diagnoses in MATLAB and the total per record (information only).

Figure 4.21  Response times of the 388 service requests in the test bench: (a) in run order, (b) cumulative distribution

## What the results mean

•  Fidelity. Every one of the 388 records got exactly the offline ML class, in each data role (benchmark, internal test and external test: 100 % each). The seven probabilities were equal digit for digit (largest difference 0), and the dashboard's Rogers, IEC 60599 and Duval answers equal the offline results for all records. There is no mismatch to trace (integration_mismatches.csv is empty).

•  Response time. Median 78.6 ms and 95th percentile 95.4 ms over all 388 calls (range 62.1 to 157.7 ms). Without the 5 warm-up calls: 78.5 and 95.1 ms - the warm-up calls hardly matter. Figure 4.21a shows no drift over the run.

•  Compared with Step 38. From Python on the same laptop the service answered in 55.3 ms (median); through MATLAB's webwrite it takes 78.6 ms. The service and the model are the same, so the extra time is most likely on the MATLAB side of the call (webwrite and its JSON handling); it was not measured separately.

•  Whole record. The total time per record (conventional diagnoses + service + agreement flag) has median 468.7 ms and 95th percentile 548.4 ms; 11 of 388 records took more than 1 s in total, the longest 1964.1 ms (request 176, DISTEST_0059). Most of the total is the MATLAB conventional diagnosis (median 277.5 ms). The plan judges only the service request, so the total is reported for information.

•  Percentile rule. The Step 41 report gave a 95th percentile of 95.6 ms, from MATLAB's prctile, which places the percentile at position n x 0.95 + 0.5; Table 4.11 uses linear interpolation (numpy), which gives 95.4 ms. Both rules describe the same 388 values; the conclusion is the same.

# 5. Checks

| Check (roadmap: fidelity is 100 %; any mismatch traced and fixed before writing) | Result |
| --- | --- |
| Fidelity F = 1 (388 of 388 ML classes identical) | PASS |
| Probabilities and the three conventional answers identical for every record | PASS - largest difference 0 |
| Every held-out record in the log once; no extra or duplicated record; model hash identical in every row | PASS |
| No failed call | PASS - 0 of 388 |
| 95th percentile of the response time below 1000 ms | PASS - 95.4 ms |
| Chapter 4 rebuild from scratch (83 files, including Table 4.11 and Figure 4.21) | PASS - identical |
| Whole automated test suite | PASS - 154 of 154 |

# 6. Problems and fixes

•  Register numbers: the parallel MATLAB session had registered its Step 39 files as DF71-DF73, the numbers the Step 38 files had been given shortly before; its update replaced the Step 38 entries. The Step 39 entries were kept, the Step 38 files were registered again as DF79-DF81, the Step 38 update script now uses those numbers, and the Step 38 report was rebuilt as version 2. The Step 42 update script stops if one of its numbers is already used by another step.

•  The rerun of the Step 38 register script had set the glossary entry for the decision numbers back to D1-D36; that line was removed from the Step 38 script and the entry now reads D1-D40.

•  The first version of Figure 4.21 placed the legend over the slowest request; the vertical axis was extended.

# 7. Decisions

•  D40 (closed, procedural): rules of the integration evaluation - inputs and the gated conventional answers, the fidelity and match rules, the response time over all records with the warm-up calls kept (sensitivity without), the percentile rule, no confidence interval for one run on one computer, and the outputs.

# 8. Files produced

•  06_Python_ML/src/analysis/step42_integration.py; 06_Python_ML/tests/test_integration.py; make_chapter4.py (updated)

•  11_Results/tables/T4_11_integration.csv; 11_Results/figures/F4_21_response_times (PNG, PDF, CSV); 11_Results/integration/integration_comparison.csv, integration_mismatches.csv, integration_checks.json, code_manifest_step42.sha256; 11_Results/chapter4_manifest.sha256 (83 files)

# 9. What was achieved

•  Fidelity of the integrated system is 100 %: the ML class was identical to the offline result for all 388 held-out records, and so were all seven probabilities and the Rogers, IEC 60599 and Duval answers.

•  The service answered within 78.6 ms (median) and 95.4 ms (95th percentile), about one tenth of the 1 s target; no call failed.

•  Table 4.11 and Figure 4.21 exist and are rebuilt by the one-command Chapter 4 script; Stage H (integration and test bench) is complete.

# 10. Record of this step

| Item | Record |
| --- | --- |
| Step | 42 - Evaluate fidelity and response time |
| Environment | Claude Code (this chat) |
| Completed | 13 October 2026 |
| Status | Done (Stage H complete) |
| Main inputs | testbench_log.csv (DF76); ml_predictions.csv (DF25); conventional_predictions.csv (DF9) |
| Main outputs | Table 4.11 (DF82); Figure 4.21 (DF83); 11_Results/integration (DF84); this report = the integration report |
| Checks | F = 1 (388/388); p95 95.4 ms < 1000 ms; rebuild check 83/83 identical; 154 of 154 tests pass |
| Decisions | D40 (rules of the integration evaluation) |

# 11. Data and sources used in this step

Every dataset, document and file this step used is listed below with its full reference, link and fingerprint (SHA-256, first 16 characters shown). Method references are listed in the 'Method used' section. The complete record, with access dates, licences and full fingerprints, is the Data and Source Register (00_Project_Admin/Step_Reports/Data_and_Source_Register.docx and 03_Data/provenance/data_and_source_register.csv).

| ID | Reference and use in the project | Link, DOI and local file |
| --- | --- | --- |
| DF76 | testbench_log.csv: one row per held-out record (388): event, simulated time, record_id, data_role, gases as read, Rogers / IEC 60599 / Duval answers, ML status, class, 7 probabilities, confidence, model name/version/hash, agreement, simulated hot-spot, response time, conventional time, total time, warm-up flag. No true label. testbench_run_info.json: run conditions (service health and model hash before/after, schedule, machine). Use: Input of Step 42 (fidelity, response time; Table 4.11, Figure 4.21). | File: 10_Dashboard_Client/logs/testbench_log.csv; SHA-256 5CA244E1635B9169... |
| DF25 | Produced in Step 22 by step22_final_fit.py with DF24; test sets predicted once (see test_set_access.log). Use: Predicted class and class probabilities for every internal-test, IEC TC 10 and Li 2019 record. | File: 11_Results/ml/ml_predictions.csv; SHA-256 D103E8CA1B21C49A... |
| DF9 | Made in Step 16 by run_conventional_batch.m on data version 1.0. Use: Input of the agreement analysis (Step 18 onwards) and of the boundary-distance test (RQ2). | File: 11_Results/conventional/conventional_predictions.csv; SHA-256 30DDD34EEF12AEF6... |
| DF27 | Produced in Step 24 by step24_save_model.py: byte-for-byte copy of DF24 (decision D21). Use: The released model: loaded through model_io.load_model(); reproduces ml_predictions.csv exactly. | File: 06_Python_ML/models/dga_model_v1.joblib; SHA-256 1C46D10391429385... |
| SW1 | Python 3.12.10 with 55 pinned packages (06_Python_ML/requirements.txt). Use: Runs every data-preparation, statistics and checking program. | https://www.python.org/downloads/release/python-31210/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |
| SW6 | FastAPI 0.143.0 (web framework), Uvicorn 0.54.0 (server), Pydantic 2.14.0 (input validation), HTTPX 0.28.1 (HTTP client for tests and the service check); Python packages pinned in 06_Python_ML/requirements.txt. Use: Runs the diagnosis service of Step 38 and its tests. | https://fastapi.tiangolo.com/; File: 06_Python_ML/requirements.txt; SHA-256 594BC0CB122EED99... |
| DF82 | Produced by 06_Python_ML/src/analysis/step42_integration.py from DF76 (test-bench log), DF25 (ML predictions) and DF9 (conventional predictions, column result); decision D40. Use: Table 4.11 of the thesis (research question on the integrated framework). | File: 11_Results/tables/T4_11_integration.csv; SHA-256 BF088B87D907AAEB... |
| DF83 | Two panels: (a) response time of every request in run order with median, 95th percentile and warm-up calls; (b) cumulative distribution with the 1000 ms target. .pdf and .csv (plotted numbers) beside the .png. Use: Figure 4.21 of the thesis. | File: 11_Results/figures/F4_21_response_times.png; SHA-256 69233376E33A00E8... |
| DF84 | integration_checks.json (fidelity counts, time statistics, pass flag), integration_comparison.csv (one row per held-out record: offline and logged answers, match flags, response time), integration_mismatches.csv (records that differ; header only when none). Use: Evidence for the 100 % fidelity requirement (Analysis Plan Section 10). | File: 11_Results/integration/integration_checks.json; SHA-256 E0A82DBFBE794FAE... |
| DF85 | 06_Python_ML/src/analysis/step42_integration.py, 06_Python_ML/tests/test_integration.py and make_chapter4.py (Step 42 added to the one-command rebuild; MATLAB outputs protected). Use: Fingerprints of the Step 42 code. | File: 11_Results/integration/code_manifest_step42.sha256; SHA-256 5F91A8FF0D7D61DF... |
| DF47 | Produced in Step 32 by make_chapter4.py: SHA-256 of every Chapter 4 table and figure file rebuilt from saved results. Use: Fingerprints of all Chapter 4 tables and figures; rebuild check identical. | File: 11_Results/chapter4_manifest.sha256; SHA-256 F1D43B16A64ABE13... |

# 12. How this helps the next steps

Next step: Step 43 (Claude Code): write Chapters 3 to 5 in Word (12 pt, 1.15 spacing) using only the tables and figures in 11_Results; every number must trace to a saved file and nothing marked TO VERIFY may remain.

•  Chapter 4 (framework performance) can report that the dashboard gives exactly the offline answers and responds well within interactive limits, so every accuracy result of Chapter 4 also describes the integrated tool.

•  Every planned Chapter 4 table (4.1-4.13) and figure (4.1-4.24) now exists in 11_Results; Figure 4.4, Table 4.10 and Figures 4.18-4.20 and 4.22 were made in MATLAB (Steps 17 and 35-41).

# 13. Open items and limitations

•  The times are from one run on one laptop with the service on the same computer; a utility network would add network delay. They describe this set-up, not a general product.

•  The conventional diagnoses in MATLAB take longer than the ML request (median 277.5 ms against 78.6 ms), as noted in Step 41; this was not investigated because it does not affect any result. The total per record stays below 1 s for 95 % of records, but 11 records took longer (up to 1964.1 ms); the plan sets the 1 s target for the service request, not for the whole record.

•  The scope is all 388 held-out records (D39); the fidelity is also given for each data role, so the 187 internal-test and benchmark records can be reported alone if the researcher prefers.

•  The service is started by hand (run_service.ps1) before the dashboard or the test bench is used.

# 14. Abbreviations and terms used in this report

Every abbreviation and technical term that appears in this report is explained below. The fault types follow the definitions of IEC 60599 (clause 5.2). The full list for the whole project is kept in 00_Project_Admin/abbreviations_glossary.csv.

| Abbreviation or term | Meaning | Plain explanation |
| --- | --- | --- |
| MPhil | Master of Philosophy | The research degree this thesis is written for. |
| UMaT | University of Mines and Technology, Tarkwa | The university where the thesis is submitted. |
| DGA | Dissolved Gas Analysis | Measuring the gases dissolved in transformer oil to find faults inside the transformer without opening it. |
| ppm | parts per million | Amount of gas in the oil; 1 ppm = 1 microlitre of gas in 1 litre of oil. |
| H2 | hydrogen | Gas formed mainly by partial discharges (low-energy electrical activity) in the oil. |
| PD | partial discharges | Small electrical discharges that only partly bridge the insulation (corona type, can form X-wax, or small sparking punctures in paper). |
| D1 | discharges of low energy | Sparking or tracking: larger punctures in paper, carbonised paper surface or carbon particles in oil. |
| T1 | thermal fault below 300 °C | Overheating in which the paper has turned brownish. |
| IEC | International Electrotechnical Commission | The world body that publishes electrical standards, such as IEC 60599. |
| IEC 60599 | IEC guide to the interpretation of dissolved and free gas analysis | The international standard that defines the fault types and the IEC gas-ratio method. |
| IEC TC 10 | IEC Technical Committee 10 (fluids for electrotechnical applications) | The committee that wrote IEC 60599; its database of 117 inspected faulty units is this thesis's main benchmark. |
| Rogers ratios | older gas-ratio method by R.R. Rogers | A ratio table that names faults from three gas ratios; kept in IEEE C57.104. |
| Normality gate | rule that lets conventional methods answer 'Normal' | If all gases are below their typical values, the conventional methods give Normal instead of a fault (decision D3). |
| ML | machine learning | Computer methods that learn the link between gas values and fault type from labelled examples. |
| Benchmark | fixed reference test set | The IEC TC 10 cases whose faults were confirmed by inspection; every method is scored on them. |
| Internal test set | Dissanayake unseen test file | 70 records (61 independent of the benchmark) kept away from training. |
| External test set | Li (2019) dataset | 201 records from a different source (86 independent of the benchmark), used to test the models on new data. |
| Primary and sensitivity analysis | main analysis and its repeat under another reasonable choice | The sensitivity analysis shows whether the conclusion changes when a choice is made differently. |
| SHA-256 | Secure Hash Algorithm, 256-bit | A file's digital fingerprint: if one byte of the file changes, the fingerprint changes. |
| Median, quartiles | middle value and the values a quarter and three quarters of the way up | Describe typical gas levels without being pulled by extreme values. |
| CSV | comma-separated values | A plain-text table file that any program can read. |
| PNG, PDF, dpi | image file, printable document file, dots per inch | Figures are saved as PNG at 300 dpi (sharp for printing) and as PDF. |
| docx | Microsoft Word document | The format of these reports. |
| Python | programming language | Used for data preparation, machine learning and statistics (Claude Code). |
| venv | virtual environment | A private copy of Python and its libraries that belongs to this project only. |
| pytest | Python testing tool | Runs the automated checks that prove the data rules hold. |
| MATLAB | MATLAB (MathWorks) | Numerical programming environment; used for the conventional methods and the dashboard (MATLAB Agentic Toolkit). |
| Simulink, Simscape | MATLAB's block-diagram modelling tool and its physical-modelling library | Used to model the transformer's operating conditions (Simulink Agentic Toolkit); it never makes gas values. |
| D1-D40 (decisions) | numbered project decisions | Decisions recorded in 00_Project_Admin/decisions_log.md; not the same as the fault codes D1 and D2. |
| Roadmap | the 45-step project plan | Project_Roadmap.docx: every step, its environment and its outputs, done strictly in order. |
| Analysis Plan | Expected Results and Analysis Plan | The approved document that fixes the measures, tests, tables and figures before results are seen. |
| TO VERIFY | not yet checked against the original source | Marks any value or fact that must still be confirmed before final use. |
| Feature set (F1-F4) | the inputs given to a model | F1 log gases, F2 gas percentages, F3 log-ratios and Duval percentages, F4 all of them (Analysis Plan 5.1). |
| Class probability | model's confidence in each class | For every record the model gives a probability for each of the seven classes; they add up to 1 and the largest is the prediction. |
| joblib | Python file format for saved models | Stores the fitted pipeline (preprocessing and model together) so it can be reloaded and give exactly the same predictions. |
| NaN (not measured) | Not a Number, used here for a gas that was not measured | A marker for a missing value. It is different from 0 ppm: 0 ppm means the gas was measured and not found, NaN means nobody measured it, so no ratio or percentage can be calculated from it. |
| Simulink | MathWorks block-diagram simulation environment | Software in which the model is drawn as blocks and lines and simulated over time. |
| Hot-spot temperature | Temperature of the hottest part of the winding | The winding temperature that mostly decides how fast the paper insulation ages; it is the top-oil temperature plus a load-dependent rise. |
| Held-out record | A record of the master table that is not used for development | A record kept aside (benchmark, internal test or external test) so that the methods are judged on data they did not learn from. |
| Agreement flag | Lamp that says whether the conventional methods agree with the ML diagnosis | Green: all three conventional methods give the same class as ML. Amber: at least one does not. Grey: no ML answer. |
| webwrite | MATLAB function that sends data to a web service | How the dashboard sends the five gas values to the FastAPI service and receives the ML class. |
| Warm-up call | One of the first calls to the service, which can be slower than the later ones | The first few requests set up the connection; they are flagged in the log so that they can be excluded or kept openly. |
| Response time | Time between sending a request to the service and receiving the answer | How long the engineer waits for the ML diagnosis; reported as the median and the 95th percentile. |
| HTTP | Hypertext Transfer Protocol | The message format of the web; the dashboard sends a request and the service sends back an answer with a status code (200 = OK, 422 = input refused). |
| JSON | JavaScript Object Notation | A plain-text format for named values, e.g. {"H2": 200}; requests and answers of the service are written in it. |
| FastAPI | Python framework for web services | The library used to build the diagnosis service; it also checks every input against the declared rules. |
| Endpoint | one address of a web service | For example POST /diagnose (send a sample, get a diagnosis) or GET /health (is the service alive?). |
| 95th percentile (p95) | the value below which 95 % of the measurements lie | Used for the response time: 95 of every 100 requests are answered at least this fast. |
| Fidelity | share of records for which the service gives exactly the offline answer | F = matches / records sent (Analysis Plan Eq. 47); the requirement is 100 %. |
| Cumulative distribution | share of measurements at or below each value | Read across from a time on the horizontal axis to see what percentage of requests were answered at least that fast. |
| Test bench | the integrated system run over every held-out record | Simulink model, MATLAB dashboard functions and the Python service working together, with every answer and its time written to a log (Step 41). |